Table of Contents

I.

II.

III.

IV.

V.

VI.

Introduction…………………………………………………….....…1

Safety Precautions…………………………………………………...2

Storage and Installation……………………………………………..4

Standards and Specifications……………………………………….5

Wiring……………………………………………………………..…8

Instruction of the Digital Operator……………………………….14

VII. Commissioning……………………………………………………..19

VIII. Function List………………………………………………………..20

IX.

X.

XI.

Descriptions of Functions………………………………………….27

Care & Maintenance, Fault Information and Troubleshooting..66

Selection of Peripheral Devices and Disposition………………....72

XII. Appendices…………………………………………………………76

This Instruction Manual is subject to changes due to product upgrading. No further notice

will be given.

I. Introduction

Thank you for purchasing and using the RLP series multi-function and high performance

inverter.

Please read carefully the operation manual before putting the inverter to use, so as to

correctly install and operate the inverter, give full play to its functions and ensure the

safety. Please keep the operation manual handy for future reference, maintenance,

inspection and repair.

In case of any problems that can not be solved during your use of our product, please

contact our local distributors at any time or contact with our company directly. Since the

inverter is a kind of electrical and electronic product, it must be installed, tested and

adjusted with parameters by specialized engineering persons of motors. The marks of

and other symbols in the manual remind you of the safety and

prevention cautions during the handling, installation, running and inspection. Please

follow these instructions to make sure the safe use of the inverter. In case of any doubt,

please contact our local agent for consultation. Our professional persons are willing and

ready to serve you.

The manual is subject to change without notice.

II. Safety Precautions

The RLP series multi-function and high performance inverter has been strictly and well

packed before ex-work. After your purchase, please examine the product package to see

whether any components are lost during the transportation, and whether the product

specifications and models comply with the machine you purchased before the unpacking.

Contact the supplier in case of any problem.

2.1 Examination after unpacking

1. The machine is provided with an instruction manual and a warranty card.

2. Examine the nameplate on the inverter side to confirm it is the product you

purchased.

2.2 Safety precautions

Danger indicates wrong use may kill or injure people.

Caution indicates wrong use may damage the inverter or mechanical system.

Note: The grades of caution will probably lead to severe results due to different

conditions. Please follow the notes, as they are very important for personal safety.

Danger















Be sure to turn off the input power supply before wiring.

Do not touch any internal electrical circuit or component when the charging lamp

is still on after the AC power supply is disconnected, which means the inverter

still has high voltage inside and it is very dangerous.

Do not check components and signals on the circuit boards during the operation.

Do not dissemble or modify any internal connecting cord, wiring or component

of the inverter by yourself.

Do not operate the switch button with wet hand, so as to prevent electrical shock.

Be sure to make correct ground connection of the earth terminal of the inverter.

Never remodel it or exchange control boards and components by yourself. It may

expose you to an electrical shock or explosion, etc.

Caution



















Do not make any voltage-withstanding test with any component inside the

inverter. These semi-conductor parts are subject to the damage of high voltage.

Never connect the AC main circuit power supply to the output terminals U.V W

of the inverter.

The inverter and the braking resistor are under high temperature when the power

supply is connected or soon after it is disconnected, do not touch them, so as to

prevent burning.

Voltage imposed on all terminals should conform to the voltage indicated in the

instruction manual, so as to prevent explosion or damage.

The main electric circuit boards of CMOS and IC of the inverter are subject to

the effect and damage of static electricity. Don't touch the main circuit boards.

Installation, testing and maintenance must be performed by qualified

professional personnel.

The inverter should be discarded as industrial waste. It is forbidden to burn it.

Please examine and commission the inverter prior to use if it is saved for long

time.

Setting for high speed operation of the inverter can be made easily. Before the

setting is changed, examine whether the motor and its mechanical performances

are suitable for high speed running.

2.3 Precautions during transportation and storage

Caution























Do not carry the front cover of the inverter directly when handling. It should be

handled with the base to prevent the fall-off of the front cover and avoid the

dropping of the inverter, which may possibly cause the injuries to people and the

damages to the inverter.

Mount the inverter on a metal or other noncombustible material to avoid the risk

of fire.

Install the inverter in a safe location, avoiding high temperature, direct sunlight,

humid air or water.

Keep the inverter from the reach of children or persons not concerned.

The inverter can only be used at the places accredited by our company. Any

unauthorized working environment may have the risks of fire, gas explosion,

electric shock and other incidents.

Install a heat sink or other cooling device when installing more than one inverter

in the same enclosure, so that the temperature inside the enclosure be kept below

40°C to avoid overheat or the risk of fire.

Be sure to turn off the power supply before dissembling or assembling the

operation key panel and fixing the front cover to avoid bad contact causing faults

or non-display of the operator.

Do not install the inverter in a space with explosive gas to avoid the risk of

explosion.

If the inverter is used at or above 1,000m above seal level, the cooling efficiency

will be worse, so please run it by de-rating.

Do not install any contactor and other components of capacitor or varistor on the

output side of the inverter. Otherwise it will cause malfunctions and damages of

components of the inverter.

Do not install any switch component like air circuit breaker or contactor at the

output of the inverter. If any of such components must be installed because of the

requirements of process and others, it must be ensured that the inverter has no

output when the switch acts. In addition, it is forbidden to install any capacitor

for improvement of power factor, or any varistor against thunder at the output.

Otherwise it will cause malfunctions, tripping protection and damages of

components of the inverter. Please remove them as shown in the below diagram.





It will affect the service life of the inverter if a contact is connected to the front

end of input of the inverter to control its starts and stops. Generally it is required

to control it through FOR or REV terminals. Special attention should be paid to

its use in the case of frequent starts and stops.

Please use an independent power supply for the inverter. Do avoid using the

common power supply with an electrical welder and other equipment with strong

disturbance. Otherwise it will cause the protection or even damage of the

inverter.

Before the Power-up



Check to make sure that the voltage of the main circuit AC power supply matches the

input voltage of the inverter.

The symbol

represents ground terminals. Be sure to make correct ground

connection of the earth terminals of the motor and the inverter for safety.



No contactor should be installed between the power supply and the inverter to be

used for starting or stopping of the inverter. Otherwise it will affect the service life of

the inverter.

During the Power-up



Do not plug the connectors of the inverter during the power up to avoid any

surge into the main control board due to plugging, which might cause the

damage of the inverter. Always have the protective cover in place before the

power up to avoid electrical shock injury.

During the Operation









Never connect or disconnect the motor set while the inverter is in running.

Otherwise it will cause over-current trip and even burn up the main circuit of the

inverter.

Never remove the front cover of the inverter while the inverter is powered up to

avoid any injury of electric shock.

Do not come close to the machine when the fault restart function is used to avoid

anything unexpected. The motor may automatically restart after its stop.

The function of STOP Switch is only valid after setting, which is different from

the use of emergent stop switch. Please pay attention to it when using it.

III. Storage and Installation

1. Storage

 It must be stored in a dry place without rubbish or dust.

 The suitable temperature for storage is between -20℃ and +65 ℃.

 The relative humidity required is 0-95% without condensation.

 There is no corrosive gas or liquid in the storage ambience.

 It's better to lay the inverter on a rack and keep it in a proper package.

 It is better not to store the inverter for long time. Long time storage of the

inverter will lead to the deterioration of electrolytic capacity. If it needs to be

stored for a long time, make sure to power it up one time within a year and the

power-up time should be at least five hours. When powered up, the voltage must

be increased slowly with a voltage regulator to the rated voltage value.

2. Installation Site and Environment

 Ambient temperature -5℃ to 40℃ with good ventilation.

 Free from the interference of electromagnetic noise.

 No water drop, stream, dust, cotton, and metallic particles.

 Free from oil, salt or corrosive gas.

 Free from vibration.

 Free from high temperature and large humidity, no rainfall, humidity <90% (no

condensation).

 Prohibited from use in inflammable, humid and explosive liquid or solid places.

Attention: The ambient conditions of the inverter will affect its service life.

3. Installation Space and Direction

 There must be enough space left around the inverter for easy maintenance and

cooling. See Diagram.

 The inverter must be installed vertically with the smooth ventilation for effective

cooling.

 If there is any instability when installing the inverter, please put a flat board

under the inverter bottom base and install it again. If the inverter is installed on a

loose surface, stress may cause damage of parts in the main circuit, so as to

damage the inverter.

 The inverter should be installed on non-combustible materials, such as iron

plate.

 If several inverters are installed, upper and lower, together in one cabinet, please

add heat dissipation plates and leave enough space between the inverters.

IV. Standards and Specifications

| 1. Specifications Type | Input Voltage | Power (KW) | Inverter Capacity (KVA) | Output Current (A) | Suitable (Motor) |
| --- | --- | --- | --- | --- | --- |
| RLPM10 00D423A | One & Three Phase 220V 50Hz | 0.4 | 1.0 | 2.5 | 0.4 |
| RLPM10 00D7523A | One & Three Phase 220V 50Hz | 0.75 | 2.0 | 5.0 | 0.75 |
| RLPM10 01D523A | One & Three Phase 220V 50Hz | 1.5 | 2.8 | 7.0 | 1.5 |
| RLPM10 00D443A | 3Φ380V 50Hz | 0.4 | 1.2 | 1.2 | 0.4 |
| RLPM10 00D7543A | 3Φ380V 50Hz | 0.75 | 2.2 | 2.7 | 0.75 |
| RLPM10 01D543A | 3Φ380V 50Hz | 1.5 | 3.2 | 4.0 | 1.5 |

| RLPB1 0 03D743A | 3Φ380V 50Hz | 3.7 | 6.8 | 8.5 | 3.7 |
| --- | --- | --- | --- | --- | --- |
| RLPB1 0 05D543A | 3Φ380V 50Hz | 5.5 | 10 | 12.5 | 5.5 |
| RLPB1 0 07D543A | 3Φ380V 50Hz | 7.5 | 14 | 17.5 | 7.5 |
| RLPB1 0 001143A | 3Φ380V 50Hz | 11 | 19 | 24 | 11 |
| RLPB1 0 001543A | 3Φ380V 50Hz | 15 | 26 | 33 | 15 |
| RLPB1 0 18D543A | 3Φ380V 50Hz | 18.5 | 32 | 40 | 18.5 |
| RLPB1 0 002243A | 3Φ380V 50Hz | 22 | 37 | 47 | 22 |
| RLPB1 0 003043A | 3Φ380V 50Hz | 30 | 52 | 65 | 30 |
| RLPB1 0 003743A | 3Φ380V 50Hz | 37 | 64 | 80 | 37 |
| RLPB1 0 004543A | 3Φ380V 50Hz | 45 | 72 | 91 | 45 |
| RLPB1 0 005543A | 3Φ380V 50Hz | 55 | 84 | 110 | 55 |

| RLPA 10 01D543A | 3Φ380V 50Hz | 1.5 | 3.2 | 4.0 | 1.5 |
| --- | --- | --- | --- | --- | --- |
| RLPA 10 02D243A | 3Φ380V 50Hz | 2.2 | 4.0 | 5.0 | 2.2 |
| RLPA 10 03D743A | 3Φ380V 50Hz | 3.7 | 6.8 | 8.5 | 3.7 |
| RLPA 10 05D543A | 3Φ380V 50Hz | 5.5 | 10 | 12.5 | 5.5 |
| RLPA 10 07D543A | 3Φ380V 50Hz | 7.5 | 14 | 17.5 | 7.5 |
| RLPA10 001143A | 3Φ380V 50Hz | 11 | 19 | 24 | 11 |
| RLPA 10 001543A | 3Φ380V 50Hz | 15 | 26 | 33 | 15 |
| RLPA 10 18D543A | 3Φ380V 50Hz | 18.5 | 32 | 40 | 18.5 |
| RLPA 10 002243A | 3Φ380V 50Hz | 22 | 37 | 47 | 22 |
| RLPA 10 003043A | 3Φ380V 50Hz | 30 | 52 | 65 | 30 |
| RLPA 10 003743A | 3Φ380V 50Hz | 37 | 64 | 80 | 37 |
| RLPA 10 004543A | 3Φ380V 50Hz | 45 | 72 | 91 | 45 |
| RLPA 10 005543A | 3Φ380V 50Hz | 55 | 84 | 110 | 55 |
| RLPA 10 007543A | 3Φ380V 50Hz | 75 | 116 | 152 | 75 |
| RLPA 10 009043A | 3Φ380V 50Hz | 90 | 134 | 176 | 90 |
| RLPA 10 011043A | 3Φ380V 50Hz | 110 | 160 | 210 | 110 |
| RLPA 10 013243A | 3Φ380V 50Hz | 132 | 193 | 253 | 132 |
| RLPA 10 016043A | 3Φ380V 50Hz | 160 | 230 | 304 | 160 |
| RLPA 10 018543A | 3Φ380V 50Hz | 185 | 260 | 340 | 185 |
| RLPA 10 020043A | 3Φ380V 50Hz | 200 | 290 | 380 | 200 |
| RLPA 10 022043A | 3Φ380V 50Hz | 220 | 325 | 426 | 220 |
| RLPA 10 025043A | 3Φ380V 50Hz | 250 | 481 | 480 | 250 |
| RLPA 10 028043A | 3Φ380V 50Hz | 280 | 427 | 560 | 280 |
| RLPA 10 030043A | 3Φ380V 50Hz | 300 | 450 | 580 | 300 |
| RLPA 10 031543A | 3Φ380V 50Hz | 315 | 460 | 605 | 315 |
| RLPA 10 034543A | 3Φ380V 50Hz | 345 | 502 | 660 | 345 |
| RLPA 10 037543A | 3Φ380V 50Hz | 375 | 544 | 715 | 375 |
| RLPA 10 040043A | 3Φ380V 50Hz | 400 | 582 | 765 | 400 |
| RLPA 10 041543A | 3Φ380V 50Hz | 415 | 604 | 795 | 415 |

| Type | Input Voltage | Power (KW) | Inverter Capacity (KVA) | Output Current (A) | Suitable (Motor) |
| --- | --- | --- | --- | --- | --- |
| RLPA10 00D423A | One & Three Phase 220V 50Hz | 0.4 | 1.0 | 2.5 | 0.4 |
| RLPA 10 00D7523A | One & Three Phase 220V 50Hz | 0.75 | 2.0 | 5.0 | 0.75 |
| RLPA 10 01D523A | One & Three Phase 220V 50Hz | 1.5 | 2.8 | 7.0 | 1.5 |
| RLPA 10 02D223A | One & Three Phase 220V 50Hz | 2.2 | 4.4 | 11 | 2.2 |
| RLPA 10 03D723A | One & Three Phase 220V 50Hz | 3.7 | 6.8 | 17 | 3.7 |
| RLPA 10 00D443A | 3Φ380V 50Hz | 0.4 | 1.2 | 1.2 | 0.4 |
| RLPA 10 00D7543A | 3Φ380V 50Hz | 0.75 | 2.2 | 2.7 | 0.75 |

| 2. General Specifications Inverter Series |  | RLP Series |
| --- | --- | --- |
| Control Mode |  | SPWM |
| Input Power |  | 380V Power supply: 380±15% 220V Power supply: 220±15% |
| 5-Digits Display & Status Indicator Lamp |  | Displaying frequency, current, revolution, voltage, counter, temperature, forward or reserve running, and fault, etc. |
| Communication Control |  | RS-485 |
| Operation Temperature |  | -10~40℃ |
| Humidity |  | 0-95% Relative Humidity (without dew) |
| Vibration |  | Below 0.5G |
|  | Range | 0.10~400.00Hz |
|  | Accuracy | Digital: 0.01% (-10-40℃) ; Analog: 0.1% (25±10℃) |
|  | Setting Resolution | Digital: 0.01Hz; Analog: 1%o of Max. Operating Frequency |
|  | Output Resolution | 0.01Hz |
|  | Keyboard Setting Method | Press directly to set |
|  | Analog Setting Method | External Voltage 0-5V, 0-10V, 4-20mA,0-20mA |
|  | Other Functions | Frequency lower limit, starting frequency, stopping frequency, three skip frequencies can be respectively set. |
|  | Ramp Control | Selectable 4-speed steps ramp-up and down time (0.1-6500s). |
|  | V/F Curve | Set V/F curve at will |
|  | Torque Control | Torque increase is settable by max. 10.0%. The starting torque can reach 150% at 1.0Hz. |
|  | Multi-Inputs | 6 multi-function input terminals for 8-speed steps control, program operation, switching of 4-speed Ramp, UP/DOWN function, counter, external emergency stop and other functions. |
|  | Multi-Outputs | 5 multi-function output terminals for displaying of running, zero speed, counter, external abnormity, program operation and other information and warnings. |
|  | Other Functions | AV R (auto voltage regulation), Deceleration stop or free-stop, DC brake, auto reset and restart, frequency track, PLC control, traverse function, drawing control, auto energy-savings, carrier adjustable by max. 16KHz, etc. |
|  | Overload Protection | Electronic relay protection motor Drive (for constant torque 150%/1 min; for the kinds of fan 120%/1min.) |
|  | FUSE Protection | FUSE broken, motor stops. |
|  | Over-voltage | DC Voltage > 400V for 220V class DC Voltage > 800V for 380V class |
|  | Low Voltage | DC Voltage < 200V for 220V class DC Voltage < 400V for 380V class |
|  | Instant Stop and Restart | Restarted by frequency track after instantaneous stop. |
|  | Stall Prevention | Anti-stall during Acc/Dec run |
|  | Output End Shorts | Electronic circuit protecting |
|  | Other Functions | Fin over-heat protection, restriction of reverse running, direct start after power on, fault reset, parameter lock PID, one-drive-more, etc. |

Frequency Control

General Control

Protection

Functions

V. Wiring

（1）Introduction of Wiring Terminals

（2）Arrangement of Main Circuit Terminals

（3）Introduction of RLPA and RLPB Series Main Circuit Terminals

(4) Introduction of RLPA and RLPB Series Control Terminals

| Symbol | Function Description | Factory Setting |
| --- | --- | --- |
| FOR | Multi-Input 1 | Forward run |
| REV | Multi-Input 2 | Reverse run |
| RST | Multi-Input 3 | Reset |
| SPH | Multi-Input 4 | High speed |
| SPM | Multi-Input 5 | Middle Speed |
| SPL | Multi-Input 6 | Low Speed |
| DCM | Common Terminal of Digital and Control Signals, IP 24 Power Ground |  |
| EV (IPV) | +12V Power Supply | Max. output current 200mA |
| IP24 | +24V Power Supply | Max. output current 200mA |
| +10 | Power Supply for Speed Setting | +10V |
| VI | Analog Voltage Frequency Command | 0—+10V corresponding to the highest operating |
| AI | Analog Current Frequency Command | 4~20mA corresponding to the highest operating frequency |
| XI | Analog Input |  |
| AO | Output Current |  |
| VO | Output voltage |  |
| ACM | Common Terminal of Analog and Control |  |
| DRV | Multi-Output 1 (Optical couple output) | DC24V/100mA |
| UPF | Multi-Output 2 (Optical couple output) | DC24V/100mA |
| FA FB FC | Multi-Output 3 (N/O or N/C) | 3A/250VAC, 3A/30VDC |
| RS+ RS- | RS485 Communication port |  |

| Symbol | Function Description |
| --- | --- |
| R.S.T | Input terminal of AC line power. (220V class, for both single/three phase, single phase connected to any two phases) |
| U.V.W | Output terminal of the inverter |
| P.Pr | Connector for braking resistor. |
| P, N | Connecting terminal of external braking bank. |
| E | Ground terminal: the third method of grounding for 220V and special grounding for 380 V of Electrical Engineering Regulations. |

(5) Introduction of RLPM Series Main Circuit Terminals

(6) Introduction of RLPM Series Control Terminals

Nameplate Description of HLP Series Inverter

| Symbol | Function Description | Factory Setting |
| --- | --- | --- |
| FOR | Multi-Input 1 | Forward run |
| REV(D2) | Multi-Input 2 | Reverse run |
| RST(D3) | Multi-Input 3 | Reset |
| SPH(D4) | Multi-Input 4 | High speed |
| SPM(D5) | Multi-Input 5 | Middle Speed |
| SPL(D6) | Multi-Input 6 | Low Speed |
| GND | Common Terminal of Digital and Control Signals, IP 24 Power Ground |  |
| +10 | Power Supply for Speed Setting | +10V |
| VI | Analog Voltage Frequency Command | 0—+10V corresponding to the highest operating |
| AI | Analog Current Frequency Command | 4~20mA corresponding to the highest operating frequency |
| VO | Output voltage |  |
| KA KB | Multi-Output 3 (N/O or N/C) | 3A/250VAC, 3A/30VDC |

| Symbol | Function Description |
| --- | --- |
| R.S.T | Input terminal of AC line power. (220V class, for both single/three phase, single phase connected to any two phases) |
| U.V.W | Output terminal of the inverter |
| P.Pr | Connector for braking resistor. |

(5) Basic Connection Diagram

The wiring of the inverter is divided into two parts, main circuit terminal connections

and control circuit terminal connections. The user can see the main circuit terminals

and the control circuit terminals after removing the cover of enclosure. The terminals

must be connected correctly as the following wiring circuit diagrams.

The following diagram shows the factory standard connection of RLP series.

(6) Precautions on Wiring

1)   For the main circuit wiring:



















While wiring, the sizes and specifications of wires should be selected and the

wiring should be executed according to the electrical engineering regulations to

ensure the safety.

It is better to use shielded wire or wire and conduit for power cord and ground the

shielded layer or two ends of wire conduit.

Be sure to install a Non Fuse Breaker (NFB) between the power supply and the

input terminals (R.S.T). (If using ground fault circuit interrupter, please choose

one corresponding to high frequency).

Never connect AC power to the output terminal (U.V.W) of the inverter.

Output wires mustn't be in touch of the metal part of the inverter enclosure, or it

will result in earth short-circuit.

Phase-shifting capacitors, LC, RC noise filters, etc, can never be connected to the

output terminals of the inverter.

The main circuit wire must be enough far away from other control equipments.

When the wiring between the inverter and the motor exceeds 15 meters for 220V

class or 30 meters for 380V class, much higher dV/dT will be produced inside the

coil of the motor, which will cause the destruction to the interlay or insulation of

the motor. Please use a dedicated AC motor for the inverter or add a reactor at the

inverter.

Please lower the carrier frequency when there is a longer distance between the

inverter and the motor. Because the higher the carrier frequency is the bigger the

leakage current of high-order harmonics in the cables will be. The leakage current

will have unfavorable effect on the inverter and other equipment.

VI. Instruction of the Digital Operator

Introduction of RLPA Series Digital Operator

Introduction of RLPM Series Digital Operator

Introduction of RLPB Series Digital Operator (3.7KW-7.5KW)

Introduction of RLPB Series Digital Operator (11KW-18.5KW)

2. Indicator Lamps

1) Description of RLPA and RLPB Series Indicator Lamp Status

| Indicator lamp | Status | Description |
| --- | --- | --- |
| FOR | on | The motor is in forward rotation. |
| REV | on | The motor is in reverse rotation. |
| HZ | on | Displaying set frequency or output |
| A | on | Displaying output current. |

2) Description of RLPM Series Indicator Lamp Status

3) Description of RLPM Series Display Items

4) Description of RLPA and RLPB Series Display Items

| Indicator lamp | Status | Description |
| --- | --- | --- |
| FOR RUN | on | The motor is in forward rotation. |
| REV RUN | on | The motor is in reverse rotation. |
| FOR STOP | on | The motor is stopped. |
| REV STOP | on | The motor is stopped. |

| ROTT | on | Displaying rated motor revolution |
| --- | --- | --- |
| A ROTT | on | Displaying AC or DC voltage. |
| HZ ROTT | on | Displaying counting value. |
| HZ A ROTT | on | Displaying internal temperature of the |

5) Description of RLPA and RLPB Series Digital Operation

| Procedures | Display | Indicator Lamp | Explanation |
| --- | --- | --- | --- |
| Power up, Operation of power |  |  | Self detect when power-up, display version no. (Flashing) and finally set frequency. |
| PROG | PD000 |  | Enter programming Display the function of PD000 |
| SET | 000.00 |  | Display the contents of PD000 |
|  | 50.00 END-50.00 PD000 050.00 |  | Change the content of PD000 Confirm changed value. Display END 50.00 PD001 Black from programming. |

Note: (1)

means flashing;

means bright;

(2) For monitoring AC, DC, F and other items, they can be only switched and

displayed after the parameter setting;

(3) When it is powered up again after a power breakdown, the inverter will

display the screen previous to the power breakdown after its self-detection.

|  | 50.00 |  | Display running and operating frequency |
| --- | --- | --- | --- |
|  |  |  | Display running and operating frequency |
|  | A005.0 |  | Monitor screen switching, display output current |
|  | 01440 |  | Monitor screen switching, display rotation speed |
|  |  |  | Switch back to main screen, display set frequency |
|  |  |  | Switch of For./Rev. rotation, display the status of Rev rotation |
|  | 050.00 |  | Switch to adjustable frequency |
|  | 030.00 |  | Adjust set frequency, i.e. the value of PD000 |
|  | 030.00 |  | Determine the changed value, input to PD003 |
|  |  |  | Stop |

VII. Commissioning

1.









Important Checks before the Commissioning

If there is any wrong with connected wires, pay special attention to the terminal

of U.V.W. (Make sure the power supply wires are connected to R.S.T.)

If there is any metal powder or wires left on the base plate of the inverter or the

terminal block, which may cause short circuit.

If screws are tightly locked and if the connecting parts are loose.

If there is any short circuit or earth fault at outputs.

2. Commissioning Methods

The procedure of the operator is factory set up for the control mode of RLP series.

The commissioning can be carried out through the digital operator.

Generally, the commissioning can be conducted at 5.00 Hz.

VIII. Function List

Parameter and Function List (Part 1)

Category

Code

Function

Set Range & Function Explanation Factory Setting

PD000

Parameter Lock

0: Invalid; 1: Valid

0

PD001

Control Method

0.

Operator

0

1.

External terminal

PD002

Selection of Frequency

2.

Communication port

0

Basic

Parameters

Setting

1. External terminal

2. Communication port

3. Operator potentiometer

PD003

Main Frequency

0.01~400.00 Hz

*

PD004

PD005

Base Frequency        0.01~400.00 Hz

Max Operating Frequency 10.00~400.00Hz

50.00

50.00

PD006

PD007

PD008

PD009

PD010

PD011

PD012

PD013

PD014

PD015

PD016

PD017

PD018

PD019

PD020

PD021

PD022

Intermediate Frequency

Min. Frequency

Max. Voltage

Intermediate Voltage

Min. Voltage

Frequency Lower

Reserved

Parameter Reset

Accel. Time 1

Decel. Time 1

Accel. Time 2

Decel. Time 2

Accel. Time 3

Decel. Time 3

Accel. Time 4

Decel. Time 4

Reserved

0.01~400.00 Hz

0.01~20.00Hz

0.1V-*

0.1V-*

0.1V-50.0V

0.00~400.00 Hz

8 Restore the factory setting.

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

0.1~6500.0S

2.50/3.00

0.50

220/380

*

*

0

00

*

*

*

*

*

*

*

*

PD023

PD024

PD025

Inverse  Rotation

Allowed

Invalid Stop Key

Starting Mode

not 0: Inverse rotation not allowed

1: Inverse rotation allowed

0: STOP invalid

1: STOP valid

0: Start from Starting Frequency

1: Frequency track start

1

1

0

Applicable

Parameters

PD026

PD027

PD028

PD029

Stopping Mode

Startup Frequency

Stop Frequency

Startup Brake Time

0: Decelerating stop

1: Coasting stop

0.1~10.0Hz

0.1~10.0Hz

0~25.0

0

0.5

0.5

0.0

0.

Operator

PD030

PD031

PD032

PD033

Stop Brake Time

DC Brake Base

Frequency Track Time

Frequency Track Current

0~25.0

0.0~20.0%

0.1~20.0S

0.1~200.0S

0.0

2.0

5.00

150.0

Base

PD034

Voltage Rise Time of

0.1~10S

0.5

Frequency Track

PD035-

PD040

Reserved

PD041

PD042

PD043

Carrier Frequency

Jogging Frequency

S Curve Time

0~15

0.00~400.00Hz

0~6500S

*

5.00

0

| Parameter and Function List (Part 2) Category | Code | Function | Set Range & Function Explanation | Factory Setting |
| --- | --- | --- | --- | --- |
| Input and Output Terminal s | PD044 | FOR(D1) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 02 |
| Input and Output Terminal s | PD045 | REV(D2) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 03 |
| Input and Output Terminal s | PD046 | RST(D3) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 14 |
| Input and Output Terminal s | PD047 | SPH(D4) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 22 |
| Input and Output Terminal s | PD048 | SPM(D5) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 23 |
| Input and Output Terminal s | PD049 | SPL (D6) Function | 0:Invalid; 1:Run; 2:For rotation;3: Rev rotation;4:Stop; 5: FOR/REV.; 6:Jog; 7: Jog For rotation;8:Jog Rev Rotation; 9: External control time 1; 10: External control timer 2;11: Reserved; 12: Overheat of heat sink or motor; 13: Emergent stop; 14: Reset; 15~16; Reserved; 17: Accel/Decel time select 1; 18: Accel/Decel time select2; 19: Multi-speed 1; 20: Multi-speed 2; 21: Multi-speed 3; 22: High speed; 23: Middle speed; 24: Low speed; 25: PID Allowed; 26: Reserved; 27: Up; 28: Down; 29: Traction allowed; 30: Reserved; 31: Pulse counter; 32: Pulse counter reset | 24 |
| Input and Output Terminal s | PD050 | Y1 Output Function | 0: Invalid; 1: Run; 2: Zero Speed Indication; 3: Fault indication; 4: DC Braking indication; 5:Set Frequency reach; 6: In Accel; 7: In Decel.; 8: Arbitrary Frequency 1 reach; 9: Arbitrary Frequency 2 reach;10: Motor Overload Alarm; 11: Over-torque Alarm; 12:Inverter Overload Alarm; 13: Counter Reach; 14~16: Reserved; 17: Low Voltage Alarm; 18: Internal Control Multi-speed End Indication; 19: Internal Control Multi-speed Process End Indication; 20~26: Reserved; 27: Traction End Indication; 28: PID Low Limit Alarm Indication; 29: PID Up Limit Alarm Indication; 30: Reserved; 31: Braking Resistor Act; 32: Fan act indication | 01 |
| Input and Output Terminal s | PD051 | Y2 Output Function | 0: Invalid; 1: Run; 2: Zero Speed Indication; 3: Fault indication; 4: DC Braking indication; 5:Set Frequency reach; 6: In Accel; 7: In Decel.; 8: Arbitrary Frequency 1 reach; 9: Arbitrary Frequency 2 reach;10: Motor Overload Alarm; 11: Over-torque Alarm; 12:Inverter Overload Alarm; 13: Counter Reach; 14~16: Reserved; 17: Low Voltage Alarm; 18: Internal Control Multi-speed End Indication; 19: Internal Control Multi-speed Process End Indication; 20~26: Reserved; 27: Traction End Indication; 28: PID Low Limit Alarm Indication; 29: PID Up Limit Alarm Indication; 30: Reserved; 31: Braking Resistor Act; 32: Fan act indication | 05 |
| Input and Output Terminal s | PD052 | (FA, FB and FC Terminals) Output Function | 0: Invalid; 1: Run; 2: Zero Speed Indication; 3: Fault indication; 4: DC Braking indication; 5:Set Frequency reach; 6: In Accel; 7: In Decel.; 8: Arbitrary Frequency 1 reach; 9: Arbitrary Frequency 2 reach;10: Motor Overload Alarm; 11: Over-torque Alarm; 12:Inverter Overload Alarm; 13: Counter Reach; 14~16: Reserved; 17: Low Voltage Alarm; 18: Internal Control Multi-speed End Indication; 19: Internal Control Multi-speed Process End Indication; 20~26: Reserved; 27: Traction End Indication; 28: PID Low Limit Alarm Indication; 29: PID Up Limit Alarm Indication; 30: Reserved; 31: Braking Resistor Act; 32: Fan act indication | 03 |
| Input and Output Terminal s | PD053 | (KA and KB Terminals) Output Function | 0: Invalid; 1: Run; 2: Zero Speed Indication; 3: Fault indication; 4: DC Braking indication; 5:Set Frequency reach; 6: In Accel; 7: In Decel.; 8: Arbitrary Frequency 1 reach; 9: Arbitrary Frequency 2 reach;10: Motor Overload Alarm; 11: Over-torque Alarm; 12:Inverter Overload Alarm; 13: Counter Reach; 14~16: Reserved; 17: Low Voltage Alarm; 18: Internal Control Multi-speed End Indication; 19: Internal Control Multi-speed Process End Indication; 20~26: Reserved; 27: Traction End Indication; 28: PID Low Limit Alarm Indication; 29: PID Up Limit Alarm Indication; 30: Reserved; 31: Braking Resistor Act; 32: Fan act indication | 00 |
| Input and Output Terminal s | PD054 | VO Output Function | Output of digital frequency signals 0-7 | 0 |
| Input and Output Terminal s | PD055 | VO Analog Output Gain | 0.0~100.0% | 0.00 |
| Input and Output Terminal s | PD056 | Skip Frequency 1 | 0.00~400.00 | 0.00 |
| Input and Output Terminal s | PD057 | Skip Frequency 2 | 0.00~400.00 | 0.00 |
| Input and Output Terminal s | PD058 | Skip Frequency 3 | 0.00~400.00 | 0.00 |
| Input and Output Terminal s | Pd059 | Skip Frequency | 0.10~10.00Hz | 0.50 |
| Input and Output Terminal s | Pd060 | Uniform Frequency 1 | 0.00~400.00Hz | 0.1 |
| Input and Output Terminal s | Pd061 | Uniform Frequency 2 | 0.00~400.00Hz | 0.00 |
| Input and Output Terminal s | Pd062 | Uniform Frequency Range Setting | 0.10~10.00Hz | 0.50 |
| Input and Output Terminal s | Pd063 | Timer 1 | 0.1~10.0 | 0.1 |
| Input and Output Terminal s | Pd064 | Timer 2 | 1~100 | 1 |
| Input and Output Terminal s | PD065 | Counting Value Set | 00~65500 | 00 |
| Input and Output Terminal s | PD066 | Intermediate Counter Value | 0~65500 | 0 |
| Input and Output Terminal s | PD067- PD069 | Reserved |  |  |

| Parameter and Function List (Part 3) Category | Code | Function | Set Range & Function Explanation | Factory Setting |
| --- | --- | --- | --- | --- |
|  | PD070 | Analog Input Select | 0: 0~10V 1: 0~5V 2: 0~20mA 3: 4~20mA 4: 0~10V, 4~20mA stacked 5: External pulse input | 0 |
|  | PD071 | Analog Filtering Constant | 0~50 | 20 |
|  | PD072 PD073 PD074 PD075 | Higher Analog Frequency Lower Analog Frequency Bias Direction at Higher Frequency Bias Direction at Lower Frequency | 0.00~400.00 Hz 0.00~400.00 Hz 0: Positive 1: Negative 0: Positive 1: Negative | 50.00 0 0 0 |
|  | PD076 | Analog Negative Bias Reverse: allowable. | 0: Not Allowable 1: Allowable | 0 |
|  | PD077 | Up/ Down Memory Function Select | 0: Not memorized 1: Memorized | 0 |
|  | PD078 | Up/ Down Stack Select | 0: 0.01Hz 1: 0.1Hz | 0 |
|  | PD079 | Reserved |  |  |
| Category | Code | Function | Set Range & Function Explanation | Factory Setting |
| Multi- Speed | PD080 | Running Mode Select | 0: General running 1: Internal control 16-speed 2: External control 4-speed 3: External control 8-speed 4: Traction 5: Interference | 0 |
| Multi- Speed | PD081 | Internal Control Multi-speed Running Mode Select | 0: Stop after running one cycle 1: Cycled running 2: Stop after automatic running one cycle (Stop interval) 3: Automatic cycled running (Stop interval) | 0 |
| Multi- Speed | PD082 | Internal Control Front 8-speed Running Direction | 0~255 (0: Positive; 1: Negative) | 0 |
| Multi- Speed | PD083 | Internal Control Back 8-speed Running Direction | 0~255 (0: Positive; 1: Negative) | 0 |
| Multi- Speed | PD084 | Internal Control Front 8-speed Accel/ Decel Time | 0~65535 | 0 |

|  | PD085 | Internal Control Back 8-speed Accel/ Decel Time | 0~65535 | 0 |
| --- | --- | --- | --- | --- |
|  | PD086 | Frequency 2 Set | 0.00-400.00Hz | 15.00 |
|  | PD087 | Frequency 3 Set | 0.00-400.00Hz | 20.00 |
|  | PD088 | Frequency 4 Set | 0.00-400.00Hz | 25.00 |
|  | PD089 | Frequency 5 Set | 0.00-400.00Hz | 30.00 |
|  | PD090 | Frequency 6 Set | 0.00-400.00Hz | 35.00 |
|  | PD091 | Frequency 7 Set | 0.00-400.00Hz | 40.00 |
|  | PD092 | Frequency 8 Set | 0.00-400.00Hz | 0.50 |
|  | PD093 | Frequency 9 Set | 0.00-400.00Hz | 10.00 |
|  | PD094 | Frequency 10 Set | 0.00-400.00Hz | 15.00 |
|  | PD095 | Frequency 11 Set | 0.00-400.00Hz | 20.00 |
|  | PD096 | Frequency 12 Set | 0.00-400.00Hz | 25.00 |
|  | PD097 | Frequency 13 Set | 0.00-400.00Hz | 30.00 |
|  | PD098 | Frequency 14 Set | 0.00-400.00Hz | 35.00 |
|  | PD099 | Frequency 15 Set | 0.00-400.00Hz | 40.00 |
|  | PD100 | Frequency 16 Set | 0.00-400.00Hz | 45.00 |
|  | PD101 | Internal Control Multi-speed Timer 1 | 0.0-6500.0S | 10.0 |
|  | PD102 | Internal Control Multi-speed Timer 2 | 0.0-6500.0S | 10.0 |
|  | PD103 | Internal Control Multi-speed Timer 3 | 0.0-6500.0S | 0.0 |
|  | PD104 | Internal Control Multi-speed Timer 4 | 0.0-6500.0S | 0.0 |
|  | PD105 | Internal Control Multi-speed Timer 5 | 0.0-6500.0S | 0.0 |
|  | PD106 | Internal Control Multi-speed Timer 6 | 0.0-6500.0S | 0.0 |
|  | PD107 | Internal Control Multi-speed Timer 7 | 0.0-6500.0S | 0.0 |
|  | PD108 | Internal Control Multi-speed Timer 8 | 0.0-6500.0S | 0.0 |
|  | PD109 | Internal Control Multi-speed Timer 9 | 0.0-6500.0S | 0.0 |
|  | PD110 | Internal Control Multi-speed Timer 10 | 0.0-6500.0S | 0.0 |
|  | PD111 | Internal Control Multi-speed Timer 11 | 0.0-6500.0S | 0.0 |
|  | PD112 | Internal Control Multi-speed Timer 12 | 0.0-6500.0S | 0.0 |
|  | PD113 | Internal Control Multi-speed Timer 13 | 0.0-6500.0S | 0.0 |
|  | PD114 | Internal Control Multi-speed Timer 14 | 0.0-6500.0S | 0.0 |
|  | PD115 | Internal Control Multi-speed Timer 15 | 0.0-6500.0S | 0.0 |
|  | PD116 | Internal Control Multi-speed Timer 16 | 0.0-6500.0S | 0.0 |
|  | PD117 | Internal Control Multi-speed Memory | 0-1 | 0 |

| Parameter and Function List (Part 4) Category | Code | Function | Set Range & Function Explanation | Factory Setting |
| --- | --- | --- | --- | --- |
|  | PD118 | Over-voltage Speed-loss Select | 0-1 | 1 |
|  | PD119 | Speed-loss Base during Accel | 0-200 | 150 |
|  | PD120 | Speed-loss Base during Constant Speed | 0-200 | 0 |
|  | PD121 | Speed-loss Decl Time during Constant Speed | 0.1-25.5 | 5 |
|  | PD122 | Speed-loss Level during Decl | 0-200 | 150 |
|  | PD123 | Over-torque Detection Mode Select | 0-3 | 0 |
|  | PD124 | Over-torque Detection Level | 0-200 | 0 |
|  | PD125 | Over-torque Detection Time | 0.1-20. 0 | 1. 0 |
|  | PD126 | Pulse Counter Memory | 0-1 | 0 |
|  | PD127- PD129 | Reserved |  |  |
| Water Supply Under Constant Pressure | PD130 | Number of Auxiliary Pump | 0-2 | 0 |
| Water Supply Under Constant Pressure | PD131 | Continuous Operating Time of Aux. Pumps | 1-9000min | 60 |
| Water Supply Under Constant Pressure | PD132 | Interlocking Time of Aux. Pumps | 1-250s | 5s |
| Water Supply Under Constant Pressure | PD133 | High Speed Running Time | 1-250s | 60s |
| Water Supply Under Constant Pressure | PD134 | Low Speed Running Time | 1-250s | 60s |
| Water Supply Under Constant Pressure | PD135 | Stopping Voltage Level | 1-150% | 95% |
| Water Supply Under Constant Pressure | PD136 | Lasting Time of Stopping Voltage Level | 1-250s | 30s |
| Water Supply Under Constant Pressure | PD137 | Wakeup Level | 1-150% | 80% |
| Water Supply Under Constant Pressure | PD138 | Sleep Frequency | 0.00-400.0 | 20. 00 |
| Water Supply Under Constant Pressure | PD139 | Lasting Time of Sleep Frequency | 1-250s | 20s |
| Water Supply Under Constant Pressure | PD140 | Reserved |  |  |
|  | PD141 | Rated Motor Voltage Rated Motor Current Motor Pole No. Rated Motor Revolution | Set upon motor nameplate | * |
|  | PD142 | Rated Motor Voltage Rated Motor Current Motor Pole No. Rated Motor Revolution | Set upon motor nameplate | * |
| Parameter s of Motor Functions | PD143 | Rated Motor Voltage Rated Motor Current Motor Pole No. Rated Motor Revolution | 02—10 | 04 |
| Parameter s of Motor Functions | PD144 | Rated Motor Voltage Rated Motor Current Motor Pole No. Rated Motor Revolution | 00—9999 | 1440 |
| Parameter s of Motor Functions | PD145 | Automatic Torque Compensation | 2.0-10. 0 | 2， 0 |
| Parameter s of Motor Functions | PD146 | Motor No-load Current | 0—100 | 40 |
|  | PD147 | Motor Slip Compensation | 0. 0-100 | 0.0 |
|  | PD148- PD149 | Reserved |  |  |
|  | PD150 | AVR Function | 0-1 | 1 |
|  | PD151 | Automatic Energy Conservation | 0-20 | 0 |
|  | PD152 | Breakdown Restart Time Stop Restart Select Allowable Breakdown Time Breakdown Restart Number | 0.2-25 | 1 |
|  | PD153 | Breakdown Restart Time Stop Restart Select Allowable Breakdown Time Breakdown Restart Number | 0：Invalid; 1：Frequency track | 0 |
|  | PD154 | Breakdown Restart Time Stop Restart Select Allowable Breakdown Time Breakdown Restart Number | 0. 1-5. 0s | 0. 5 |
|  | PD155 | Breakdown Restart Time Stop Restart Select Allowable Breakdown Time Breakdown Restart Number | 0-10 | 00 |

| Parameter and Function List (Part 5) Category | Code | Function | Set Range & Function Explanation | Factory Setting |
| --- | --- | --- | --- | --- |
| PID Paramete rs | PD156 | Proportional Constant | 0.0-1000.00% | 100% |
| PID Paramete rs | PD157 | Integral Time (I) | 0.1-3600.00s | 5. 0 |
| PID Paramete rs | PD158 | Differential Time (D) | 0.01-10.00s | 0 |
| PID Paramete rs | PD159 | Target Value | 0.0-100.00% | 0 |
| PID Paramete rs | PD160 | Target Value Select | 0: Set by the operator 1: Set by external terminals | 0 |
| PID Paramete rs | PD161 PD162 | PID Upper Limit PID Lower Limit | 0~100% 0~100% | 100% 0% |
| Commun ication Function | PD163 PD164 PD165 | Communication Address Communication Baud Rate Communication Data Method | 0-250 0-3 0-5 | 0 1 0 |
|  | PD166- PD169 | Reserved |  |  |
|  | PD170 | Display Items | 0-5 | 0 |
| Monitori ng Paramete rs | PD171 PD172 PD173 PD174 PD175 PD176 | Display Items Open Fault Clear Rated Voltage of Inverter Rated Current of Inverter Type of Inverter Standard of Inverter Frequency | 0-15 00- 10〔01means Fault Clear） Set upon Model Set upon Model 0:50Hz 1:60Hz | 0 * |
| Monitori ng Paramete rs | PD177 | Fault Record 1 | Note:----No fault record | * |
| Monitori ng Paramete rs | PD178 | Fault Record 2 | Note:----No fault record | --- |
| Monitori ng Paramete rs | PD179 | Fault Record 3 | Note:----No fault record | --- |
| Monitori ng Paramete rs | PD180 | Fault Record 4 | Note:----No fault record | ---- |
| Monitori ng Paramete rs | PD181 | Software Version No. |  | ---- |
| Monitori ng Paramete rs | PD182 | Ex-factory Date | Year Month Day | * |
|  | PD183 | Serial Number |  | * |
|  | PD184- PD250 | Reserved |  |  |

IX. Descriptions of Functions

PD000 Parameters Lock

Set Range: 0-1              Unit: 1           Factory Setting: 0

0: Invalid

1: Valid, means parameters are locked. Except for this parameter, all parameters are

not allowed to be changed.

It can prevent the wrong operations by non-professionals, thus causing unnecessary

dangers and mistakes.

It can be changed by pressing ▲ or ▼.

PD001 Control Mode Select

Set Range: 0-2              Unit: 1           Factory Setting: 0

0: Keyboard is set.

The running orders are given by the keyboard.

1: External switch input terminal programming

The running orders are given by the external terminals, which are set by 6-speed

programmable terminals.

2: Communication port is set.

The running orders are given by the communication port.

PD002 Frequency Set Select

Set Range: 0-3              Unit: 1           Factory Setting: 0

0: Keyboard set     The current operation frequency is set by the keyboard Pd003.

1: Analog set        The current operation frequency is controlled by the input

analog signals, whose type is decided by Pd070. Refer to

Pd070-Pd076 for related parameters.

2: Modbus set      The current operation frequency is set by the communication

port.

3: Operator potentiometer set   The current operation frequency is set by the

operator potentiometer.

Pd003 Main Frequency                        **

Set Range:0.00-400.00Hz Unit: 0.01Hz      Factory Setting: 0.00

In the digital operator mode, the inverter will run at the set value of Pd003.During

running, the operating frequency can be changed by pressing ▲ or ▼. During

multi-speed running, the main frequency is taken as the frequency of speed 1.

In the external control multi-speed mode, if Pd002 is set to 1, ie. given by an external

terminal, Speed 1 will be given by the analog of the external terminal.

The setting of main frequency is limited by the maximum operating frequency.

The related parameters of Pd002, Pd080, are adjustable during operation.

Pd004 Base Frequency                        **

Set Range:0.01-400.00Hz Unit: 0.01Hz      Factory Setting: 50.00

This parameter must be set according to the rated frequency of operating voltage on

the motor's nameplate. Under normal conditions, do not change the set value of base

frequency at will. If it is equipped with a special motor, this value should be set

properly according to the characteristics of the motor's parameters. Otherwise it may

cause the damage to the equipment.

Pd005 Max. Operating Frequency

Set Range:10.00-400.00Hz    Unit: 0.01Hz      Factory Setting: 50.00

This parameter determines the max operating frequency of the inverter.

Pd006 Intermediate Frequency

Set Range:0.01-400.00Hz Unit: 0.01Hz      Factory Setting: 2.50

Note: ** means this parameter is adjustable during the operation.

This parameter is set for an intermediate frequency value of arbitrary V/F curve. If it

is set improperly, it will cause over-current or under-torque of the motor, or even

tripping of the inverter.

The intermediate frequency set value is restricted by the base frequency set value.

Pd007 Min. Frequency

Set Range:0.01-20.00Hz   Unit: 0.01Hz      Factory Setting: 0.50

This parameter decides the minimum startup frequency in the V/F curve.

Pd008 Max. Voltage

Set Range:0.1-*          Unit: 0.1V        Factory Setting: 220/380V

This parameter should be set according to the rated value of the motor's nameplate.

The factory setting is 380V for 380V class motor and 220V for 220V class motor. The

setting range of this parameter is restricted by the voltage rating of the inverter. In

case of the motor relatively far away from the inverter, this set value can be increased

properly.

Pd009 Intermediate Voltage

Set Range:0.1-510.0V     Unit: 0.1V        Factory Setting: 15/27.5

This parameter is set for an intermediate voltage value of arbitrary V/F curve. If it is

set improperly, it will cause over-current or under-torque of the motor, or even

tripping of the inverter. When the intermediate frequency is increased, the voltage will

increase the output torque and at the same time also the output current. When

changing this parameter, please pay attention to monitoring the output current to avoid

the inverter's tripping due to over-current.

The factory setting of 220V class inverter is 15 and that for 380V is 27.5.

This set value of intermediate voltage is limited by the set value of max voltage.

When the voltage is increasing to a certain value at intermediate frequency, the torque

compensation will lose its function. When adjusting this parameter, the output current

of the inverter should be increased from low to high slowly according to the load of

machines until it meets the starting requirement. Do not be quick to increase it by

large amplitude. Otherwise it might cause the tripping of the inverter or the damage of

the machines.

Pd010 Min. Voltage

Set Range:0.1-380.0V     Unit: 0.1V        Factory Setting: *

This parameter determines the minimum startup voltage in the V/F curve.

The factory setting is 8 for 220V class inverter and 13.5 for 380V class inverter.

The setting value of Pd010 is restricted by the voltage of maximum operating

frequency.

Pd011 Lower Limit Frequency

Set Range:0.00-400.00    Unit: 0.01Hz      Factory Setting: 0.00

The lower limit frequency is set to avoid the wrong operation of site workers, thus

preventing the motor from overheating or mechanical breakdowns due to too low

frequency.

The lower limit frequency must be lower that the setting value of upper limit

frequency.

The following table is the factory setting for RLPA, RLPB and RLPM series V/F curve,

acceleration/ deceleration time, and filtering wave.

Note: ① Ramp Time 2 = Ramp Time 1 x 2

② Ramp Time 3 = Ramp Time 2 x 2

③ Ramp Time 4 = Ramp Time 3 x 2

④ Min.Voltage Value = Intermediate Voltage Value/2

⑤ The intermediate frequency is 2.5 for the system of 50Hz.

⑥ The intermediate frequency is 3.0 for the system of 60Hz.

Pd012 Reserved

The following are several curves and set values often used for reference. Specific

curves must be set according to concrete characteristics of mechanical load.

Curve of constant torque

Curve of lower torque

Curve of higher torque

Pd013 Parameter Reset

Set Range: 00-10        Unit: 1           Factory Setting: 00

When the value for a parameter is set improper or is abnormal for some reasons, this

parameter can be set to 08 to restore it to the factory setting and then reset. After the

parameters are locked (in case of Pd000=1), the parameters can't be reset. They can

only be reset after unlock. For related parameters, refer to P013.

PD014 Accel. Time 1

**

Set Range: 01—

P015   Decel. Time 1

Set Range: 01—

P016   Accel. Time 2

Set Range: 01—

P017   Decel. Time 2

Set Range: 01—

P018   Accel. Time 3

Set Range: 01—

6500.0S

6500.0S

6500.0S

6500.0S

6500.0S

Unit: 01S

Unit: 01S

Unit: 01S

Unit: 01S

Unit: 01S

Factory Setting: *

**

Factory Setting: *

**

Factory Setting: *

**

Factory Setting: *

**

Factory Setting: *

P019

Decel. Time 3

***

Set Range: 01—    6500.0S     Unit: 01S    Factory Setting: *

P020   Accel. Time 4                              **

Set Range: 01—    6500.0S     Unit: 01S    Factory Setting: *

P021   Decel. Time 4                              **

Set Range: 01—    6500.0S     Unit: 01S    Factory Setting: *

Ramp-up time means the time needed for the inverter to increase the frequency from

0Hz to the maximum operating frequency (See tl in the diagram). Ramp-down Time

means the time needed for the inverter to decrease the frequency from the maximum

operating frequency to 0Hz (See t2 in the diagram).

M Series inverter has altogether 4 Ramp Times. For Ramp Time 2.3.4, the user can

select the different ramp up or down time through the external terminals or switching

of ramp time according to the actual needs. In the internal control multi-speed

operation, different ramp time can be selected through easy PLC.

Generally the default of the inverter is Ramp Time 1, which is factory set depending

on the model. Ramp Time 4 is for the jogging ramp time. For the factory setting of

parameters refer to the table in CD006.

The related parameters: Pd044-Pd049, Pd084, Pd085

Pd022 Factory Reserved

Pd023 Rev Rotation Disable

Set Range: 0-1          Unit: 1           Factory Setting: 1

0: Rev rotation disables.

1: Rev Rotation enables.

This function is suitable for the motor, which is not allowed to rotate reversely, to

prevent workers from false operation. When the reverse rotation is disabled, the motor

can only rotate forward, not reverse.

Pd024 Stop Key Invalid

Set Range: 0-1          Unit: 1           Factory Setting: 1

0: STOP key invalid.

1: STOP key valid.

This parameter set is only valid when Pd001 is set to l or 2.

Pd025 Starting Mode

Set Range: 0-1

Unit: 1

Factory Setting: 0

Two starting modes are available for the needs of different equipment.

0: Start from the starting frequency.

When Pd 029 is set to 0, i.e. DC braking is invalid at start, it starts running from the

starting frequency. When Pd029 is set to any non-zero value, i.e. DC braking is valid

at start, it first performs a DC braking at start, and then starts from the starting

frequency.

For the related parameters refer to Pd027, Pd029 and Pd031.

1: Start by frequency track

This setting can be used for the restarting of large inertia load. When restarting, the

inverter will trace the former frequency from the set frequency downward. In case of

large inertia equipment, when restarting, it can implement the running command and

track the former frequency right away without waiting for the complete stop of the

equipment to save time.

Note: When the inverter is restarted by frequency track, it will start tracking the

frequency from its set frequency downward, and search it at the highest speed. When

restarting, the current becomes higher, and over-current or stall may occur. So

attention must be paid to the adjustment of current level of frequency track. Generally,

Pd033 is adjusted around 100. The concrete value can be set according to the

characteristics of mechanical load.

Pd026 Stopping Mode

Set Range: 0-1          Unit: 1           Factory Setting: 0

0: Decelerating Stop

When Pd030 is set to 0, DC braking is invalid. When DC braking is invalid, the

inverter will decelerate to the stopping frequency, and then stop outputs, and the

motor will coast to stop. When CD142 is set to any non-zero value, DC braking is

valid, and the inverter will first decelerate to the stopping frequency, and then stop by

DC braking.

DC braking at stop is usually used for high position stop or for positioning control. It

must be noticed that frequent uses of DC braking will cause over-heat of the motor.

For the related parameters refer to Pd028, Pd030 and Pd031.

1: Coasting Stop

When the inverter receives a STOP command, it will immediately stop output and the

motor will coast to stop. When the coasting stop mode is selected, DC braking is

invalid.

Pd027 Starting Frequency

Set Range: 0.1-10.0Hz   Unit: 0.1Hz       Factory Setting: 0.5

Starting frequency is the initial frequency when the inverter is started. If the starting

frequency is set to 5.0Hz, the inverter will run between 5.0 Hz and the maximum

operating frequency after its start at 5.0Hz. The actual maximum operating frequency

is limited by the upper limit of frequency.

For the related parameters, refer to Pd025, Pd029 and Pd031.

Pd028 Stopping Frequency

Set Range: 0.1-10.0Hz   Unit: 0.1Hz       Factory Setting: 0.5

When stopping, the inverter will decrease its frequency to the stopping frequency and

then stop running or start DC braking to stop.

If Pd029 is set to 0, DC braking is invalid at stop and the inverter will stop running. If

Pd029 is set for valid, the inverter will stop by DC braking after it reduces to the value

of Pd028.

For the related parameters, refer to Pd028, Pd029 and Pd030.

Pd029 DC Brake Time at Start

Set Range: 0.0-25.0S     Unit: 0.1S

Factory Setting: 0.0

This parameter is set for DC Braking at start and the lasting time of DC Braking

current to the motor. If it is set to zero, it means DC braking is invalid.

DC braking at start is normally used in the application, in which the load is movable

when the machine is at stop, such as winRLPill. Because of the load existing before the

inverter drives, the motor is often in coasting with an uncertain rotation direction. So

the DC braking can be executed before starting the motor to prevent the inverter from

tripping.

When Pd025 is set to 0, it is valid.

For the related parameters, refer to Ph025, Ph029 and Ph031.

Pd030 DC Brake Time at Stop

Set Range: 0.0-25.0      Unit: 0.1S

Factory Setting: 0.0

When this parameter is set to any non-zero value it starts DC brake at stop and sends

the DC braking time to the motor. DC braking at stop is often used for a high-level

stop or positioning control. When this parameter is set to zero, it closes DC braking at

stop.

This setting is valid when PD026 is set to 0.

For the related parameters, refer to Ph026, Ph028 and Ph031.

Pd031 DC Braking Voltage Level

Set Range: 0.0-20.0%           Unit: 0.1%        Factory Setting: 2.0

This parameter is set for the DC braking voltage to the motor at start and stop. It can

be adjusted for different braking voltage. When adjusting the parameter, it must be

increased slowly from lower value to high value, until the sufficient braking torque is

achieved.

The voltage at maximum frequency is 100% voltage.

Pd032 Frequency Track Time

Set Range: 0.0-20.0S     Unit: 0.1S        Factory Setting: 5.0

This parameter is set as frequency track time when the inverter is started by frequency

track after an external abnormality or temporary power breakdown. For starting or

stopping of some large inertia load, if restarting a machine after its complete stop, it

will waste much time because of its large inertia of load. But if the frequency track is

started, it is not necessary to wait for the machine to come to a full stop for restart.

The inverter will trace the frequency from high to low with the set frequency. After

searching, it will continue to accelerate to reach the set frequency.

Pd033 Current Level for Frequency Track

Set Range: 0-200%              Unit: 1%      Factory Setting: 150

When the inverter is tracing the frequency, this set value is taken as the level for

output current. When the output current is higher than this level, the inverter will

decrease the frequency to restore the current below the level and then it will execute

the frequency track again.

Pd034 Voltage Rise Time during Frequency Track       Factory Setting: 0.5

When the starting mode of the inverter is set to frequency track, there is a process of

voltage rise during the frequency track. When the voltage is rising rapidly, the current

will be higher and the tracking process will be faster. When the voltage is rising

slowly, the current will be lower and the tracking process will be slower. In general

practice, this value of Pd034 is set lower for the inverter of smaller power and set

higher for the inverter of larger power.

Pd035-Pd040

Reserved

Pd041 Carrier Frequency KHz (Note: 0—15 corresponds to 0—20K Hz)

Set Range: 0-15         Unit: 1           Factory Setting: 5

The carrier frequency is related to the electromagnetic noise, as well as to the heating

capacity of the inverter and the interference of the environment. See the table as

follows:

Table of Carrier Frequency

The higher the carrier is, the lower the electromagnetic noise of the motor will be, but

the stronger its interference to other systems will be and the greater the heating

capacity of the inverter will have. Under higher ambient temperature and heavier load

of the motor, the carrier frequency should be decreased properly to improve the heat

characteristics of the inverter.

The factory setting of carrier frequency is depending on the model.

Pd042 Jogging Frequency                      **

Set Range: 0.0-400.00    Unit: 0.01         Factory Setting: 5.00

The parameter set can realize the jogging function when the inverter is tested. The

jogging operation can be only achieved through the external terminals, which can be

set by multi-input terminals. Jogging frequency is limited by the frequency

upper/lower limits. While the jogging function is implemented, other running

commands are invalid. The ramp-up time of jogging frequency is set by Ramp-up

Time 4. When the jog button is released, the inverter will stop output immediately. In

case of jogging function, please set the corresponding multi-input terminals to 07 or

08.

This function is only valid at stop. It is invalid at running.

For the related parameters, refer to Pd044~Pd049.

Pd043 S-Curve Time

Set Range: 0-6500S      Unit: 1           Factory Setting: 1

This parameter can be set for no impact slow start or slow stop of the inverter when

starting or stopping. When starting S-curve, the inverter will make accelerating or

decelerating curve of different speed rates according to Ramp Time.

Pd044

Pd045

Pd046

Pd047

Pd048

Pd049

D1 Terminal Function

D2 Terminal Function

D3 Terminal Function

D4 Terminal Function

D5 Terminal Function

D6 Terminal Function

Factory Setting: 02

Factory Setting: 03

Factory Setting: 14

Factory Setting: 22

Factory Setting: 24

Factory Setting: 23

Set Range: 00-32

01: RUN

02: FOR

03: REV

04: STOP

05: FOR/REV

06: JOG

Unit:

Running. It can be combined with other terminals to compose

multiple control modes.

Forward Rotation

Reverse Rotation

Stopping

Switching of FOR/REV rotation

Jogging

07: Jog FOR Rotation

08: Jog REV Rotation

09: External Control When the contact is closed, the timer will start and begin to

Timer 1 Start:

count time. When the timer reaches the set point, the

corresponding multi-inputs will act.

10: External Control

Timer 2 Start

12: Over-heat of heat This contact can be used to detect over-heat of the heat sink or

sink or motor:

13: Emergent Stop

motor to protect the motor and inverter.

It can receive external emergent stop command or other fault

signals.

14: RST Reset.       This terminal can be used for reset after a fault is removed.

15~16: Reserved.

17: Ramp Time 1

18: Ramp Time 2

19: Multi-speed 1

20: Multi-speed 2

21: Multi-speed 3

22: High speed

23: Middle speed

This terminal can be used to select the ramp time of the

inverter.

4 kinds of ramp time are available for choice.

8-speed setting can be composed through Multi-speed 1, 2, 3.

High, middle and low speed can compose three kinds of

operation mode.

With different frequencies. In the three terminals the high-end

signal has priority. Low, Middle and High Speed are

determined respectively by Frequency 2, 3, 4.

24: Low speed

25: PID Valid

When this contact is closed, PID function starts. PID Function

start is only valid during operation.

26:

Internal control This contact can realize the internal control multi-speed clear

multi-speed clear reset reset.

27: UP Function      When the switch of this terminal acts, the frequency setting of

the inverter will be increased or decreased by one unit.

When the switch of the terminal is held, the frequency will

increase or decrease rapidly to a point and then increase or

decrease at even speed. When the power is up again after the

power breakdown the changed frequency will not be

memorized.

28: Down Function

29: Drawing Start     When this contact is triggered the drawing action starts.

31: Counter Pulse     When this terminal is set for the counter it can receive the

pulse signal of ≤250HZ and counts.

32: Counter Reset    When this contact acts it will clear the present counting values

displayed, restore C00 and restart counting.

Explanation:

1. Three multi-function terminals can be used for the connection method of

three-wire system for the realization of switching of FOR/REV rotation, which is

extensively applied in the cases of FOR/REV switching of photoelectric switches.

① Select D1, D2 and D3.

② Parameter setting:

Pd001=1 for external control; Pd044=02 for FOR rotation;

Pd045=03 for REV Rotation; Pd046=04 for Stop.

③ Action Description:

When triggering D1, the inverter will rotate forward (start);

When triggering D2, the inverter will rotate reverse;

When pressing STOP , the inverter will stop.

2. RUN, DCM, F/R can be used for Start, Stop and switching of FOR/REV:

① Select FOR, REV and RST.

② Parameter setting: Pd001=1 for external control;

Pd044=01 for RUN function;

Pd045=05 for F/R switch;

When triggering FOR, the inverter will rotate forward (start); When triggering REV,

the inverter will rotate reverse.

3. Description of Ramp Time 1 and 2:







This function is only valid when Pd080 is set to 0, 2 and 3. Under the disturbance

and internal control multi-speed, it is invalid.

Any two multi-inputs can be combined for 4 kinds of ramp time for selection.

The related multi-inputs are set for Ramp Time 1, 2. Take the terminals of D4 and

D5 as example, when Pd047 of D4 is set to 22and Pd048 of D5 is set to 23, D4

and D5 are now Ramp Time 1, 2.

4. Function description of High, Middle and low speed terminals:

Note: ( 1 ) This function is only valid when Pd080 is set to 1, i.e. for 4-Speed of

external control.

( 2 ) Ramp time is determined by Ramp Select terminal.

( 3 ) When all high, middle and low speeds have signal inputs, it will give

priority in the sequence of high, middle and low speed.

5. Description of UP and DOWN Function:

Note: ( 1 ) The function of UP and DOWN is only valid when the operator is selected

for the source of the operating frequency, i.e. Pd002=0.

( 2 ) When the UP terminal is closed, the frequency of the inverter will increase.

( 3 ) When the DOWN terminal is closed, the frequency of the inverter will

decrease.

( 4 ) When both UP and DOWN terminals are closed at the same time, the

| frequency will neither increase nor decrease. It is regarded as invalid. RUN | D6 | D5 | D4 | Result |
| --- | --- | --- | --- | --- |
| ON | OFF | OFF | OFF | Main speed, the frequency runs at the set value of Pd003. |
| ON | ON | OFF | OFF | Low speed, the frequency runs at the set value of Pd086. |
| ON | ON/OFF | ON | OFF | Middle speed, the frequency runs at the set value of Pd087. |
| ON | ON/OFF | ON/OFF | ON | High speed, the frequency runs at the set value of Pd088. |

| D4 | D5 | Result |
| --- | --- | --- |
| OFF | OFF | Ramp Time 1 |
| ON | OFF | Ramp Time 2 |
| OFF | ON | Ramp Time 3 |
| ON | ON | Ramp Time 4 |

| UP | DOWN | Result |
| --- | --- | --- |
| ON | OFF | Frequency increase |
| OFF | ON | Frequency decrease |
| ON | ON | Not increase or decrease |

( 5 ) When the frequency reaches the max operating frequency, it will stop

increasing.

( 6 ) When the frequency reaches the min frequency or its lower limit, it will

stop decreasing.

( 7 ) After a power breakdown, the set value of CD000 will be memorized

instead of the frequency.

( 8 ) When using the function of UP and DOWN, the keys of

of the panel

are valid. After changing the values, it needs to press SET (ENTER) key

for confirmation and then the inverter can implement the action.

Meanwhile, the value will write to Pd003, which will be memorized after a

power breakdown.

( 9 ) When keeping pressing UP or DOWN, the frequency will increase or

decrease rapidly to a point and then increase or decrease at even speed.

( 10 ) The value changed by UP or DOWN can be set through Pd077 for

confirmation of whether it should be memorized or not memorized. For

details, refer to Pd077.

6. Function Description of Counter:

Note: (1) The signal width triggered should not be lower than 2 msec (t1, t2>2msec) .

(2) When the counting value is reached, the corresponding multi-output contact

will act.

(3) This counter can only count again after reset.

(4) When reaching to 65535, the counter will not count again.

Pd050

Pd051

Pd052

Pd053

Y1 Output

Y2 Output

FA, FB and FC Terminal Output

KA and KB Terminal Output

Set Range: 00-32

Factory Setting: 01

Factory Setting: 05

Factory Setting: 03

Factory Setting: 00

Unit: 1

01: RUN

The contact will act when the inverter has output or

receives the running command.

02: Zero Speed

03: Fault Indication

The contact will act when the output frequency of the

inverter is less than its starting frequency.

The contact will act when the inverter detects

abnormal conditions.

04: DC Braking Indication        The contact will act when the inverter is in DC

braking.

05: Set Frequency Reach         The contact will act when the output frequency of the

inverter reaches the set frequency.

06: In Accel                    The contact will act when the inverter is in ramp-up.

07: In Decel                    The contact will act when the inverter is in

ramp-down.

08:Uniform Frequency 1 Reach    The contact will act when the output frequency of the

inverter reaches the designated frequency (Pd060).

09: Uniform Frequency 2 reach    The contact will act when the output frequency of the

inverter reaches the designated frequency (Pd061).

10: Motor Overload Alarm

11: In Over-torque Detect

The contact will act when the inverter detects

over-load of the motor.

The contact will act when the inverter detects

over-torque.

12: Inverter Over-load Alarm      The contact will act when the inverter detects

over-load.

13: Set Counter Reach           The contact will act when the inverter implements

the external counter and the counting value is equal

to the set value (Pd065).

14: Middle Counter Reach        The contact will act when the inverter implements

the external counter and the counting value is greater

than or equal to the set value (Pd066).

15: External Control Timer 1 reach The contact will act when the timer 1 reaches the set

value.

16: External Control Timer 2 reach The contact will act when the timer 2 reaches the set

value.

17: Low Voltage Alarm           The contact will act when the inverter detects low

voltage.

18: Single Step End              The contact will act and generate one pulse when the

inverter finishes a single step in implementation of

program operation.

19: Process End                 The contact will act and generate one pulse, when

the inverter finishes all the steps (i.e. after one cycle)

in implementation of program operation.

20:4~20mA Disconnected         When AI input signal is opened the contact will act.

25: Auxiliary Pump 1            This contact controls the starting and stopping of

auxiliary pumps. For details, refer to Operation of

Multi-pumps.

26: Auxiliary Pump 2

27: Drawing Reach

28: PID Lower Limit Alarm

29: PID Upper Limit Alarm

30: Braking Resistor Act

31: Electromagnetic Relay Act

32: Fan Act

The contact will act when the drawing action is

finished. The contact will automatically reset when

the inverter stops.

This contact will act when the PID feedback is

smaller than the lower limit (the set value of Pd162).

This contact will act when the PID feedback is

greater than the upper limit (the set value of Pd161).

When the inverter is in running and the DC voltage

reaches the braking voltage the contact will act.

When the contact pulls in, the corresponding

multi-function terminal will act.

When the temperature of the inverter is increased or

it is in running, this contact will act.

Pd054 VO Output

Set Range: 0-7          Unit: 1           Factory Setting: 0

Functions: Output terminal of digital frequency, generating pulse or 0—10V analog.

In combination with Pd055, it can be connected with a corresponding

instrument with the measuring range below 10 to be used for external

monitoring.

0: 0~10V analog output, corresponding to output frequency. 0~10V corresponds to

0~Maximum operating frequency.

1: 0~10V analog output, corresponding to output current. 0~10V corresponds to

0~two times of the rated current of the inverter.

2: Analog output, corresponding to DC bus voltage. 0~10V corresponds to 0~1000V

3: Analog output, corresponding to AC output voltage. 0~10V corresponds to

0~510V/255V

(Note: The machine type of three phases, 380V corresponds to 510V and the machine

type of single phase, 220V corresponds to 255V).

Pd055 VO Analog Output Gain

Set Range: 0.0-100.0%   Unit: 0.1%        Factory Setting: 100.0

This parameter can be used to adjust the output voltage value of Multi-output 6 to

adapt to frequency meters with different measuring range and also used to correct a

frequency meter. For example, for an externally connected frequency meter with the

measuring range of 0~5V, a multi-function terminal can be used to display its

operating frequency. Then it can be corrected with this parameter. It can be achieved

by setting Pd055=50.

Pd056 Skip Frequency 1

Pd057 Skip Frequency 2

Pd058 Skip Frequency 3

Set Range: 0.00—400.00 Hz

Pd 059 Skip Frequency Range

**

Unit: 0.01Hz Factory Setting: 0.00

**

Set Range: 010—10.00 Hz

Unit: 0.01Hz

Factory Setting: 0.50

These three frequency skipping points are set for avoiding a mechanical resonance

point. In case of Pd059=0, all skip frequencies are invalid. The actual skip frequency

range is two times that of Pd059, as shown in the above diagram.

Pd060

Pd061

Uniform Frequency 1

Uniform Frequency 2

**

Set Range: 0.00—400.00 Hz    Unit: 0.01 Hz Factory Setting: 0.00

Pd062     Uniform Frequency Range                   **

Set Range: 0.10—10.00 Hz     Unit: 0.01 Hz Factory Setting: 0.50

When the output frequency is more than the uniform frequency, the corresponding

multi-outputs will act. The uniform frequency range acts as a hysteresis loop. When

the inverter is in the operation of multi-pumps, Pd060 (Uniform Frequency 1) is used

as high speed frequency and CD062 is set as low speed operating frequency. The

definitions of the corresponding multi-function contacts are changed.

Pd063

Timer 1 Time

Pd064

Set Range : 01 ~ 10.0

Timer 2 Time

Unit: 1

Factory Setting: 01

Set Range : 1 ~ 100        Unit: 1      Factory Setting: 1

Timer 1 is a timer of 01s ~ 10.0s and Timer 2 is a timer of 1s ~ 100s. When the timer

start at multi-inputs is closed (on) the timer starts to count time. When it reaches the

set time the corresponding multi-output contact will act. When the timer start is

opened (off) the timer time at the multi-output will be reset.

For example, set Pd063=5.0s. When the external control terminal (Multi-Input) is

valid, the output terminal will be valid after five (5.0) seconds, the signal of which can

be used to control other corresponding signals.

Pd065

Counting Value                            **

Set Range: 0-65500             Unit: 1      Factory Setting: 0

An external terminal of multi-function can be used as a trigger for the counter. When

the counter reaches the set value of Pd065, the corresponding multi-output contact

will act. After the counter is cleared and reset, it will start counting again. A proximity

switch or optoelectronic switch can be used for the triggering signals.

Pd066

Pulse Intermediate Counting Value

Set Range: 0-65500             Unit: 1

Refer to Pd065.

Factory Setting: 0

Pd067-Pd069

Reserved

Pd070

Analog Input Select

Set Range: 0-4             Unit: 1          Factory Setting: 0

0: 0~10V  1: 0~5V 2: 0~20mA  3: 4~20mA   4: 0-10V and 4-20mA stacked

This parameter can be set for different analog input signals.

When Pd070=4, the output frequency =1/2 (U/Umax + I/Imax ) x 50Hz

Among which: U: Analog Voltage; Umax: Maximum Analog Voltage;

I: Analog Current; Imax: Maximum Analog Current.

Pd071

Analog Filtering Constant

Set Range: 0-50            Unit: 1          Factory Setting: 20

The setting of this parameter is related to the analog responding speed. The higher the

value of Pd071 is set, the lower the analog responding speed will be.

Pd072

Higher Analog Frequency

Set Range: 0.00-400.00Hz

Unit: 0.01Hz Factory Setting: 50.00

Pd073

Lower Analog Frequency

Set Range: 0.00-400.00Hz

Unit: 0.01Hz Factory Setting: 0.00

Pd074

Bias Direction at Higher Frequency

Set Range: 0-1              Unit: 1      Factory Setting: 0

Pd075     Bias Direction at Lower Frequency

Set Range: 0-1              Unit: 1      Factory Setting: 0

0: Positive direction

1: Negative direction

Bias direction means the instruction of FOR/REV rotation command. Positive bias

indicates forward rotation while negative bias indicates reverse rotation.

For details, refer to the diagram in Pd076.

Pd076

Analog Negative Bias Reverse

Set Range: 0-1              Unit: 1      Factory Setting: 0

0: Negative bias Rev is not allowable.

1: Negative bias Rev is allowable.

The parameter group is set for the measuring range and zero point of the external

analog terminals and can be combined for any kind of curve to control the operation

of the motor.

Setting: Pd073=50 Pd075=1

Pd072=50 Pd074=0

Pd076=1

Note: this curve can be easily used in complicated

applications in combination with other curves. When

using it the instruction of FOR/REV run from external

terminals is still valid. When switching, the curve will turn

reverse.

Setting: Pd073=50 Pd075=0

Pd072=0 Pd074=0

Pd076=0

Note: this curve is a kind of special application of

reverse ramp setting. When using transmitter for the

control of pressure, temperature and others and while

the control has higher pressure and output signals, but

requiring the corresponding commands of stop or

deceleration on the inverter, this curve can satisfy the

demand properly.

Setting: Pd073=10 Pd075=1

Pd072=40 Pd074=0

Pd076=1

Note: this method is used extensively. The user can use

it flexibly.

Setting: Pd073=10 Pd075=1

Pd072=40 Pd074=0

Pd076=0

Note: this curve is the extension of the above curve.

2V~10V (4.8mA~20mA) corresponds to 0Hz~40HZ; the

signal of 0V~2V (4~4.8mA) is invalid. It can be used to

avoid noise disturbance. In harsh environment it is better

not to use signals below 1V for setting the operating

frequency of the inverter.

Pd077

UP/DOWN Function

Set Range: 0-1            Unit: 1           Factory Setting: 0

0: Not memorized  1: Memorized

This parameter can be set for the selection of whether the values changed by the UP

or DOWN shall be memorized or not after stop. The changed values whether to be

memorized or not means when they are changed by UP or DOWN during operation

and the inverter is restarted after stop, these changed values shall be memorized or not

after restart. When Pd077 is set to 0, the changed value will not be memorized and

when it is set to 1, the changed values will be memorized. The set values of Pd003

will be memorized after restart.

For the related parameters, refer to Pd044-Pd049.

Pd078

UP/DOWN Speed

Set Range: 0-1            Unit: 1           Factory Setting: 0

0: 0.01Hz. Minimum UP/DOWN speed is 0.01Hz.

1: 0.1Hz. Minimum UP/DOWN speed is 0.1Hz.

Through the changes of this set value, the UP/DOWN speed unit can be adjusted to

meet the needs of different customers.

Pd079

Pd080

Reserved

Operation Mode

Set Range: 0-5            Unit: 1           Factory Setting: 0

0: Normal operation, i.e. the inverter is running in the normal control mode.

1: Internal control multi-speed (16-speed)

Note: ① 8-Speeds is made by adding the main frequency to the 7-speeds.

② The ramp up/down time is determined by Pd084 and Pd085.

③ The running time is set by Pd101~Pd116 timer. The unused control part can

be set as 0 by the timer.

④ The running direction of various frequencies can be set by Pd082 and

Pd083.

⑤ When the internal control multi-speed is running, the running time and

direction are set by the internal parameters. The external time switch and

FOR/ REV. switch are invalid.

2. External control 4-speed (Refer to the function description and diagram of three

terminals of high, middle and low speed in Pd044~Pd049)

3. External control multi-speeds

Note: ① It is only valid to realize the external control 8-Speeds operation when

Multi-inputs are set for Multi-speed 1, 2, 3 and Pd080 is set to 3.

② Multi-speed 1, 2, 3 can be used to make up 7-Speeds and adding the main

frequency.

③ The frequencies of Speed Step 1 ~ Step 7 are determined by Pd086~Pd092.

④ Each ramp time is determined by D1-D6 external terminal.

⑤ The directions of each program operation are determined by the external

multi-function terminals.

⑥ The main frequency can be set in two ways. One method is to set it through

Pd003 and another is to set it through the potentiometer. When Pd002 is set

to 1, the frequency of Main Frequency is set by the potentiometer.

For the related parameters, refer to Pd003, Pd002 and Pd086~Pd092.

4. Disturbance (Traverse function)

This is a special parameter in the chemical fiber and printing and dying industries to

realize the traverse function. Except the commands of stop, external faults and

emergency stop all other commands are not accepted at running.

Note: ① The frequency at each inflection point is determined by Pd003 and Pd086.

② Skip Frequency is determined by Pd092.

③ Running Time is determined by Timer Pd101 and Pd102.

④ The related parameters: Pd003, Pd086~Pd116.

| 5. Drawing Multi-function Terminals |  |  | Results |
| --- | --- | --- | --- |
| Multi-speed 1 | Multi-speed 2 | Multi-speed 3 |  |
| OFF | OFF | OFF | Main frequency and frequencies are determined by Pd003 or potentiometer. |
| ON | OFF | OFF | Multi-speed 1 and frequency are determined by Pd086. |
| OFF | ON | OFF | Multi-speed 2 and frequency are determined by Pd087. |
| ON | ON | OFF | Multi-speed 3 and frequency are determined by Pd088. |
| OFF | OFF | ON | Multi-speed 4 and frequency are determined by Pd089. |
| ON | OFF | ON | Multi-speed 5 and frequency are determined by Pd090. |
| OFF | ON | ON | Multi-speed 6 and frequency are determined by Pd091. |
| ON | ON | ON | Multi-speed 7 and frequency are determined by Pd092. |

This is a special parameter for the constant speed of unwinding and rewinding. By

using this function, the linear speed constant in certain accuracy can be realized.

Note: ① Through triggering of the external multi-function terminal, the drawing

action begins.

② In implementation of the drawing action, the actual running time is

T=Pd101 x 10.

③ When the drawing action is finished, the inverter will run at the constant

seed of Pd087 and the corresponding multi-output contact will act at the

same time. Until receiving the STOP command, the inverter will stop

running and the multi-output contact will reset.

Pd081

Auto PLA

Set Range: 0-3            Unit: 1           Factory Setting: 0

0: Stop after the program runs one cycle.

1: Cycling running.

2: Stop after it runs one cycle automatically (STOP for intervention).

3: Auto running and cycling (STOP for intervention)

This parameter setting is only valid when Pd080 is set to 4. For relevant Parameters,

refer to Pd003, Pd080, Pd082~Pd116.

Explanation:

1. Stop after the program runs one cycle.

When the command of auto program operation is given, the inverter will run with

each set value of internal parameters. It will run for one cycle and then stop

automatically. The inverter will not restart and run until it receives another command

of operation.

2. Cycling run.

When the command of operation is given, the inverter will run in sequence with the

frequency of every speed step and running time set by each of the internal parameters

and will recycle. During the cycling run, except the commands of stop, external faults

and emergency stop, all other commands will not be accepted.

3. Stop after it runs one cycle automatically (STOP for intervention).

Note: 1) When the command of auto program operation is given, the inverter will run

with each parameter. But it will stop first and then restart at changing of

each step and will stop automatically after running for one cycle. The

inverter will not restart and run until it receives another command of

operation.

2) The frequencies of each speed step are set by Pd003, Pd086~Pd092.

3) The running times of each speed step are set by Pd101~Pd108.

4) The running direction is set by Pd082.

Pd082

Pd083

Running Direction of First 8-speeds

Running Direction of Last 8-speeds

Set Range: 0-255            Unit: 1         Factory Setting: 0

This parameter is only valid when Pd080 is set to 1.

This parameter setting determines the running direction of each frequency of

Pd086-Pd092, and Pd003 in the program operation. The setting method is as follows:

The rotation direction is set first in the binary 8 bits mode, and then converted to a

decimal value for the setting of this parameter. For instance:

The parameter 01001010 is converted into a decimal value, that is:

Then parameter Pd082=74

Pd083 is the setting for the last 8-speed running direction (the calculation method is

same as Pd082).

Pd084

Pd085

Ram Up Time of First 8-speeds

Ram Down Time of Last 8-speeds

Set Range: 0~65535           Unit: 1S      Factory Setting: 0

This parameter is only valid when Pd080 is set to 1.

This parameter is set to determine the ramp time values of the internal control

multi-speed. The setting method is as follows:

(1) Determine each Ramp Time in the binary 2 bit mode:

| (2) Determine the Ramp time of each speed step in the binary 16 bit mode: Bit1 | Bit0 | Ramp Time |
| --- | --- | --- |
| 0 | 0 | Ramp Time 1 Pd014, Pd015 |
| 0 | 1 | Ramp Time 2 Pd016, Pd017 |
| 1 | 0 | Ramp Time 3 Pd018, Pd019 |
| 1 | 1 | Ramp Time 4 Pd020, Pd021 |

t1 Select Ramp Time 4

t2 Select Ramp Time 1

t3 Select Ramp Time 3

t4 Select Ramp Time 2

t5 Select Ramp Time 1

t6 Select Ramp Time 1

t7 Select Ramp Time 1

The setting value:

1x20+1x21+1x25+1x26=99

So Pd084 is set to 99.

Attach: 20=1 21=2 22=4 23=8

24=16 25=32 26=64 27=128

t8 Select Ramp Time 1

Pd085 is the last 8-step ramp time selection (the calculation method is same as

Pd084).

Pd086

Pd087

Pd088

Frequency 2

Frequency 3

Frequency 4

Factory Setting

Factory Setting

Factory Setting

15

20

25

Pd089     Frequency 5         Factory Setting        30

Pd090     Frequency 6         Factory Setting        35

Pd091     Frequency 7         Factory Setting        40

Pd092     Frequency 8         Factory Setting        0.50

Pd093     Frequency 9         Factory Setting        10

Pd094     Frequency 10        Factory Setting        15

Pd095     Frequency 11        Factory Setting        20

Pd096     Frequency 12        Factory Setting        25

Pd097     Frequency 13        Factory Setting        30

Pd098     Frequency 14        Factory Setting        35

Pd099     Frequency 15        Factory Setting        40

Pd100     Frequency 16        Factory Setting        45

Set Range: 0.00—400.00 Hz       Unit: 0.01 Hz

This parameter is set in combination of the multi-inputs to select 4-speeds of external

control, multi-speeds of external control or multi-speeds of internal control.

For the relevant parameters, refer to the description of Pd080, Pd086-Pd100.

Pd101

Pd102

Timer 1

Timer 2

Factory Setting

Factory Setting

10.0

10.0

Pd103     Timer 3             Factory Setting        0.0

Pd104     Timer 4             Factory Setting        0.0

Pd105     Timer 5             Factory Setting        0.0

Pd106     Timer 6             Factory Setting        0.0

Pd107     Timer 7             Factory Setting        0.0

Pd108     Timer 8             Factory Setting        0.0

Pd109     Timer 9             Factory Setting        0.0

Pd110     Timer 10            Factory Setting        0.0

| Pd111 Timer 11 Factory Setting 0.0 Step 8 |  | Step 7 |  | Step 6 |  | Step 5 |  | Step 4 |  | Step 3 |  | Step 2 |  | Step 1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| t8 |  | t7 |  | t6 |  | t5 |  | t4 |  | t3 |  | t2 |  | t1 |  |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 |

Pd112     Timer 12            Factory Setting        0.0

Pd113     Timer 13            Factory Setting        0.0

Pd114     Timer 14            Factory Setting        0.0

Pd115     Timer 15            Factory Setting        0.0

Pd116     Timer 16            Factory Setting        0.0

Set Range: 0.0—6500.0S          Unit: 0.1S

This parameter is set for the internal control multi-speeds and the running time of

drawing function.

For the relevant parameter, refer to Pd080, Pd101~Pd116.

Pd117

Auto PLC Memory Function

0-1

Factory Setting: 0

0: Not memorized

1: Memorized

This parameter is set to determine whether the inverter is to realize the suspending

function in Auto PLC mode. In case of Pd115=1, it can memorize the status in which

the inverter is running and will memorize it at stop or fail. It will continue to run when

returning to normal. In case of Pd115=0, it will not memorize.

Pd118

Over-voltage Stall Prevention

Set Range: 0-1              Unit: 1         Factory Setting: 1

0: Over-voltage stall prevention invalid

1: Over-voltage stall prevention valid.

When the inverter is in deceleration, due to the effect of load inertia, the motor will

produce a return energy to the inverter and cause the DC voltage of the inverter to

increase. So when the function of over-voltage stall prevention is started, if the DC

voltage of the inverter becomes too high, the inverter will stop decelerating till the

voltage at DC decreases below the set value, then the inverter will go on to decelerate

and the ramp-down time will be extended automatically.

Pd119

Stall Prevention Level at Ramp-up

Set Range: 0-200%              Unit: 1%   Factory Setting: 150

When the inverter is in ramp-up, due to overload or too short ramp-up time, the output

current of the inverter will go up quickly and exceed the set standard level. When this

happens, the inverter will stop accelerating. When the current returns under its set

value, the inverter will go on to accelerate.

100% current is the rated current of the motor. When this parameter is set to 0, the

stall prevention function is invalid.

Pd120

Stall Prevention Level at Constant Speed

Set Range: 0-200%              Unit: 1%   Factory Setting: 0

When the inverter is running at constant speed, due to load fluctuation and other

reasons, the current will increase. When the current exceeds its set standard value, the

inverter will lower the output frequency. When the output current returns to its normal

range, the inverter will accelerate again to its set frequency.

100% current is the rated current of the motor. When this parameter is set to 0, the

stall prevention function is invalid.

Pd121

Decel. Time for Stall Prevention at Constant Speed Factory Setting: 5.0

When the inverter is used for the loads of kinds of fan and pump, Pd119 can be set to

120. When the current of the inverter is greater than 120%, the output frequency will

decrease and the current will also decrease accordingly. After the current returns to

normal, the frequency will return to normal slowly, so as to achieve the stall

prevention function. The decreasing speed of the frequency is determined by Pd119.

For the related parameters, refer to Pd119.

Pd122

Stall Prevention Level at Deceleration

Set Range: 0-200%              Unit: 1

Please refer to Pd120.

100% current is the rated current of the motor.

Factory Setting: 150

Pd123

Over-torque Detect Mode

Set Range: 0-3                  Unit: 1     Factory Setting: 0

0: When reaching the frequency, it starts to detect over-torque and when over-torque

is detected, it continues to run.

1: When reaching the frequency, it starts to detect over-torque and when over-torque

is detected, it stops running.

2: It detects over-torque during running and when over-torque is detected, it continues

to run.

3: It detects over-torque during running and when over-torque is detected, it stops

running.

Pd124

Over-torque Detect Level

Set Range: 0-200%              Unit: 1%   Factory Setting: 0

When the output current exceeds the over-torque detection level and also exceeds half

of the set time of over-torque detection (factory setting: 1.0s), the over-torque

detection will indicate, and the corresponding multi-function alarm contact will act.

When it exceeds the set time, the inverter will turn to self-protection. When this

parameter is set to 0, the over-torque detection will be invalid.

Pd125

Over-torque Detect Time

Set Range: 0.1-20.0S              Unit: 0.1S Factory Setting: 1.0

When the inverter detects that the output current has exceeded the motor current set

value, the inverter begins to calculate the over-torque time. When the over-torque time

has exceeded half of the set detect time, the corresponding multi-function output

contact will act, and produce the over-torque alarm, while the inverter will keep

running. When the over-torque time has exceeded the set detect time (set by Pd125),

the inverter will turn to self-protection, display the fault information and stop output.

For the related parameters, refer to Pd123.

Pd126

Counter Memory

Set Range: 0-1

0: Not memorize

1: Memorize

Counter memory    , inverter memory function

Pd127-Pd129

Reserved

Pd130

Number of Auxiliary Pump

Unit: 0

Factory Setting: 0

Set Range: 0-2                  Unit: 1     Factory Setting: 0

This parameter is set for the number of auxiliary pump. The start or stop of the

auxiliary pumps is controlled by using the multi-output contacts and Auxiliary Pump

1 or Auxiliary Pump 2 is controlled through the peripheral control circuit.

Pd131

Continuous Running Time of Auxiliary Pumps

Set Range: 0-900(min)            Unit: 1    Factory Setting: 60

In case of two pumps with only one pump in duty, in order to ensure each pump to

work evenly, it will be switched to another pump when its running time reaches the

set value of Pd131.

Pd132

Interlocking Time of Auxiliary Pump

Set Range: 1-250S                Unit: 1   Factory Setting: 5S

This parameter is set to determine the interlocking time of two auxiliary pumps when

switching with each other.

Pd133

High Speed Running Time

Set Range: 1-250S                Unit: 1   Factory Setting: 60S

In the application of water supply with constant pressure, when the master pump is

running at the frequency of high speed (set by Pd060) due to larger water volume and

the high speed running time is reached, the corresponding multi-function contacts act

and the auxiliary pumps start.

Pd134

Low Speed Running Time

Set Range: 1-250S                Unit: 1   Factory Setting: 60S

In the application of water supply with constant pressure, when the master pump is

running at the frequency of low speed (set by Pd061) due to smaller water volume and

the low speed running time (Pd134) is reached, the corresponding multi-function

contacts act and the auxiliary pumps stop.

Pd133 and Pd134 must be used in combination of Pd060, Pd061 and multi-outputs.

Their main function is to increase or decrease the number of auxiliary pump.

Pd135

Stopping Voltage Level

Set Range: 0-150%                Unit: 1   Factory Setting: 95%

This parameter is set for the voltage level of the master pump entering into sleep

mode. For details, refer to the following description.

Pd136

Lasting Time of Stopping Voltage Level

Set Range: 1-250S               Unit: 1    Factory Setting: 30S

This parameter is set for the lasting time under the stopping voltage level before

entering into sleep mode.

Pd137

Wakeup Voltage Level

Set Range: 0-150%                Unit: 1   Factory Setting: 80%

This parameter is set for the wakeup voltage level from sleep to wakeup.

Pd138

Sleep Frequency

Set Range:0.00-400.00               Unit: 1 Factory Setting: 20.0

This parameter is set for the lowest operating frequency entering into sleep mode.

Pd139

Lasting Time of Sleep Frequency

Set Range: 1-250S

Unit: 1

Factory Setting: 20S

This parameter is set for the lasting time to run at sleep frequency when entering into

sleep mode.

Pd140

Reserved

Pd141

Rated Motor Voltage

Unit: 0.1V Factory Setting:*

It is set according to the rated voltage value of the nameplate of the motor. For the

inverters of 230V class, the factory setting is 220, while for the inverters of 400 V

class, the factory setting is 380.

Pd142

Rated Motor Current

Unit: 0.1A Factory Setting:*

It is set according to the rated value of the nameplate of the motor. This parameter can

be used to restrict the output current of the inverter to prevent over-current and protect

the motor. If the current of the motor has exceeded this value, the inverter of AC

motor will turn to self-protection.

Pd143

Motor Pole Number

Set Range: 02-10                    Unit: 1 Factory Setting: 04

This parameter is set for the number of the motor's pole according to the nameplate of

the motor.

Pd144

Rated Motor Revolution

Set Range: 0-9999               Unit: 1r/min Factory Setting: 1440

This is set according to the actual revolution of the motor. The displayed value is the

same as this set value. It can be used as a monitoring parameter, which is convenient

to the user. This set value corresponds to the revolution at 50Hz.

Pd145

Auto Torque Compensation

Set Range: 0.1-10.0%

Unit: 0.1% Factory Setting: 2.0%

This parameter can be set for the auto output of extra voltage when the inverter is

running to a higher torque, which can compensate for the under-torque at lower

frequency. The torque compensation should not be too big and it should be set slowly

from low to high according to the actual situation. Insufficient compensation will

result in the under-torque of the motor at lower

frequency. And over compensation will lead to too

bigger torque, which will produce a shock to the

machine and even result in a trip of the inverter under

serious situation.

Pd146

Motor No-load Current

Set Range: 0-99                   Unit: 1 Factory Setting: 40

The setting of motor no-load current will affect the value of slip compensation. The

current is 100% of the rated current of the motor.

Pd147

Motor Slip Compensation

Set Range: 0.0-10.0              Unit: 0.1 Factory Setting: 0.0

When the inverter drives the motor, the slip becomes bigger due to the increase of

load. This parameter can be set for slip compensation to decrease the slip and make

the running speed of the motor closer to the synchronous revolution.

Pd148-Pd149

Reserved

Pd150

Auto Voltage Regulation (AVR)

Set Range: 0-1                   Unit: 1  Factory Setting: 1

0: Invalid     1: Valid

When the input power is not stable and if the voltage is too high, the operation of the

motor with the power exceeding the rated voltage will cause increase of the

temperature of the motor, damage of its insulation and unstable output torque. This

auto voltage regulation can automatically stabilize the output voltage within the rated

voltage range of the motor under the condition of unstable output power supply

When this function is set to invalid, the output voltage will fluctuate.

Pd151

Auto Energy Saving

Set Range: 0-10%              Unit: 1%     Factory Setting: 0

When it is set to zero, this function is invalid. When auto energy saving function is

started, the inverter will run at the full voltage during ramp-up or -down. During the

operation at constant speed, the inverter can automatically calculate the optimum

voltage value according to the power of load and supply power to the load to achieve

the goal of energy saving.

Pd152

Fault Restart Time

Factory Setting: 0

When the inverter is set for fault restart and if it has a fault trip with the time

exceeding the set value of Pd152, the inverter will restart. When using this function,

pay more attention to the safety.

Pd153

Restart after Instantaneous Stop

Set Range: 0-1                   Unit: 1    Factory Setting: 0

0: Invalid, i.e. the inverter will not restart after an instantaneous power breakdown.

1: Start by frequency track. Refer to Pd025.

Pd154

Allowable Power-Breakdown Time

Set Range: 0.1-5.0S              Unit: 0.1S

Factory Setting: 0.5

This parameter is set for the maximum allowable power failure time. If exceeding the

set time, the inverter will continue to stop output after power on.

To restart the inverter, it needs to follow the general starting procedures.

Pd155

Number of Abnormal Restart

Set Range: 00-10                  Unit: 1

Factory Setting: 00

After the abnormal conditions (such as over-current and over-voltage) happens, the

inverter will automatically reset and restart. If the starting mode is set to normal mode,

it will start according to the normal procedures. If it is set to start by frequency track,

it will start in the frequency track mode. After starting, it will restore the set number

again if there is no more abnormality happened within 60 seconds. If there is still any

error and it reaches the set number, the inverter will stop output. It can only be started

after reset. When Pd155 is set to zero, the inverter will not carry out the functions of

automatic reset and restart.

Pd156

Proportional Constant (P)

**

Set Range: 0.0~100.00%         Unit: 0.1% Factory Setting: 100%

This proportional constant is set for the error value gain. In case of I=0, D=0, it is

only for proportional control.

Pd157

Integral Time (I)

**

Set Range: 0.1~3600.0S          Unit: 0.1S Factory Setting: 5.0S

The integral time (I) is set for the responding speed for PID. The larger the I value is

set, the slower the responding speed will be. To the contrary, if the responding speed

is quick but the integral time value is set too small, it will cause oscillation.

Pd158

Differential Time (D)

**

Set Range: 0.1~10.00S          Unit: 0.01S Factory Setting: 0

This differential time (D) is set for the depression operation of PID. The larger the D

value is, the more obvious the depression operation will be. When D is set to zero,

this function is invalid.

Pd159

Target Value

**

Set Range: 0~100.0%             Unit: 1% Factory Setting: *

This target value can be set through external voltage signal or the digital operator.

100% target value is corresponding to the analog frequency at +10V.

PID closed-loop control is usually used in the process control with physical quantity

not changing fast, such as the controls of pressure and temperature, etc. The feedback

signal is usually taken from temperature transmitter, or pressure transmitter, etc.

Under PID control, the feedback signal input path is the analog current signal of

4-20mA.

PID closed-loop control is valid when Multi-input PID is started.

PID Control Block Diagram:

General operating methods of PID control:

(1) Choose the correct transmitter (with the output specification of standard current

signal 4-20mA)

(2) Set the right target value.

(3) If the output does not have oscillation, increase the proportional constant (P).

(4) If the output does not have oscillation, decrease the integral time (Ti)

(5) If the output does not have oscillation, increase the differential time (Td).

(6) Concrete applications can be referred to the example application descriptions in

Appendix 1.

1. Suppress the Over Output

a: Decrease the differential

time (D value)

b: Increase the integral time (I

value)

2. Suppress the oscillation

a: Decrease the differential time

(D value) or set it to zero.

b:    Decrease    Proportional

Constant (P value)

Pd160

PID Target Value

**

Set Range: 0-1                   Unit:    Factory Setting: 0

The target value can be set through the selection of the panel or external analog. The

external analog is 0~10V signal or given by the potentiometer.

When Pd160=0, the target value of PID is the value set by Pd159.

When Pd160=1, the target value of PID is the value of the external analog 0-10V

(corresponding to 0-100%), the setting of Pd159 is invalid.

Pd161

PID Upper Limit

**

Set Range: 0~100%                 Unit: Factory Setting: 100%

When PID feedback value is more than the set value of Pd161, the corresponding

multi-output will act and the inverter will not stop.

Pd162

PID Lower Limit

**

Set Range: 0~100%                 Unit: Factory Setting: 0%

When PID feedback value is less than the set value of Pd162, the corresponding

multi-output will act and the inverter will not stop.

Pd163

Communication Addresses

Set Range: 00-250                Unit:    Factory Setting: 00

When the inverter is set for RS-485 Communication interface control, each of the

inverters will be set for its individual identification number.

00: No communication function.

01~250: Address for the inverters

Pd164

Communication Band Rate

Set Range: 0-3

0: 4800 b/s    1: %00 b/s   2: 19200 b/s

Unit:   Factory Setting: 1

3: 38400 b/s

Pd165

Communication Data Method

Set Range: 0-5

0: 8N1 For ASCII           1: 8E1 For ASCII

3: 8N1 For RTU             4: 8E1 For RTU

Unit: 1  Factory Setting: 0

2 :8O1 For ASCII

5: 8O1 For RTU

Pd166-Pd168

Reserved

MODBUS Communication Protocol

1. ASCII mode:

Mode of communication data

(1) STX Starting unit " : " (3AH)

(2) ADDR communication address, 8-bit data is composed of two ASC II bytes.

01~250: Address of the corresponding inverters.

(3) CMDFUNC: Function code 8-bit command















01 Read the single code data

03 Read register

04 Read input register

05 Write the single code data status

06 Write the single register

0F Write multi- code data status

10 Write multi-register

a: Read function code data

Send the data format:

“:” ADDRESS 01 ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

Note: ADDR: 0X00000--- 0X FFFF; NUM: 0X0001---0X 0020 (NUM means the

number of code data to be read)

The format of normal returned data:

“:” ADDRESS 01 BYTECOUNT DATA1 DATA2 DATA3 DATAN LRC 0X0D 0X0A

Note: BYTECOUNT = NUM/8 or BYTECOUNT = NUM/8 + 1 (taken as a whole or

whole +1)

Format of wrong returned data:

“:” ADDRESS 0X81 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. Read the status of current running of the inverter

ASII format

Send: 3A 30 31 30 30 30 35 30 30 30 31 3F 39 0D 0A

Return: 3A 30 31 30 31 30 31 30 31 46 43 0D 0A (ASII)

The returned data bite “01” (hexadecimal) is converted into 2-byte “0000 0001”, the

last one means the running status; “1” means the inverter is under REV. running (“0”

for FOR. Rotation or STOP, refer to specific description)

b. 03 read data register

Send the data format:

“:” ADDRESS 03 ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

Note: ADDR: 0--- 0XFFFF; NUM: 0X0001---0X 0020 (NUM means the number of

data register to be read)

The format of normal returned data:

“:” ADDRESS 03 BYTECOUNT DATA1 DATA2 DATA3 DATAN LRC 0D 0A

Note: BYTECOUNT = 2 * NUM

Format of wrong returned data:

“:” ADDRESS 0X83 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. Read the value of function code in Pd003 (eg. 30.00Hz)

RTU Format send: “:” 03 00 00 00 00 01 FC 0D 0A (hexadecimal)

ASCII Format send: 3A 30 33 30 30 30 30 30 30 30 3A 46 43 0D 0A (ASCII)

RTU Format data returned: “:” 01 03 02 0B B8 37 0D 0A (hexadecimal)

ASCII Format data returned: 3A 30 31 30 33 30 32 30 42 42 38 33 37 0D DA

The bite of data returned “0BB8” (hexadecimal) means P003 = 30.00

c. 04 read input data register

Send the data format:

“:” ADDRESS 04 ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

Note: ADDR: 0--- 0XFFFF; NUM: 0X0001---0X 0004 (NUM means the number of

code data to be read)

The format of normal returned data:

“:” ADDRESS 04 BYTECOUNT DATAH1 DATAL1 – DATAHN DATALN

Note: BYTECOUNT = NUM * 2

Format of wrong returned data:

“:” ADDRESS 0X84 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. The current temperature of the inverter

RTU Format send: “:” 01 04 00 06 00 01 F4 0D 0A

ASCII Format send: 3A 30 31 30 34 30 30 30 36 30 30 30 31 46 34 0D 0A

RTU data returned: 01 04 02 01 6A 8E 0D 0A

ASCII data returned: 3AC 30 31 30 34 30 32 30 31 36 41 38 45 0D 0A

The bite of data returned is 0x16A, means the temperature is 36.2

d. Write single data status

Send the data format:

“:” ADDRESS 05 ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

Note: ADDR: 0--- 0XFFFF DATA: 0X0000 or 0XFF00 (0XFF00 valid)

The format of correct returned data:

“:” ADDRESS 05 ADDRH ADDRL DATAH DATAL LRC 0X0D 0X0A

The format of wrong returned data:

“:” ADDRESS 0X85 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. Inverter running through communication control

Data sent through RTU: 01 05 00 48 FF 00 B3 “0D 0A” (hexadecimal)

Data sent through ASCII: 3A 30 31 30 35 30 30 34 38 46 46 30 30 42 33 0D 0A

(ASCII)

Data returned through RTU: 01 05 00 48 FF 00 B3 “0D 0A” (hexadecimal)

Data returned through ASCII: 3A 30 31 30 35 30 30 34 38 46 46 30 30 42 33 0D 0A

(ASCII)

e. 06 Write single data register

Send the data format:

“:” ADDRESS 06 ADDRH ADDRL DATAH DATAL LRC 0X0D 0X0A

Note: ADDR: 0--- 0XFFFF

Correct returned data:

“:” ADDRESS 06 ADDRH ADDRL DATAH DATAL LRC 0X0D 0X0A

Wrong returned data:

“:” ADDRESS 0X86 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. Write 1.84Hz into inverter P003

Data sent through RTU: 01 06 00 03 00 B8 36 0D 0A (hexadecimal)

Data sent through ASCII: 3A 30 31 30 36 30 30 30 33 30 30 42 38 33 45 0D 0A

(ASCII)

Data returned through RTU: 01 06 00 03 00 B8 79 B8 (hexadecimal)

Data returned through ASCII: 3A 30 31 30 36 30 30 30 33 30 30 42 38 33 45 0D 0A

(ASCII)

The bite of data returned is “00BB” (hexadecimal), means the setting for P003 is 1.84.

f. OF Write multi-data status

Send the data format:

“:” ADDRESS OF ADDRH ADDRL NUMH NUML COUNT DATAH1 DATAL1

DATA2H DATA2L – DATANH DATANL LRC 0X0D 0X0A

Note: ADDRR: 0X000 – 0X00FF; DATA: 0X0000 ~ 0X00FF

NUM: 0X0000 – 0X0007; COUNT: NUM/8 or NUM/8 + 1 (NUM means the number

of data to be written)

The format of correct returned data:

“:” ADDRESS OF ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

The format of wrong returned data:

“:” ADDRESS 0X8F 01 or 02 or 03 or 04 LRC 0X0D 0X0A

eg. Send REV. rotation and running command to the inverter at the same time

Data sent through RTU: 01 0F 00 48 00 03 01 00 05 9F 0D 0A (hexadecimal)

Data sent through ASCII: 3A 30 31 30 46 30 30 34 38 30 30 30 33 30 31 30 30 30 35

39 46 0D 0A

Data returned through RTU: 01 0F 00 48 00 03 A5 0D 0A (hexadecimal)

Data returned through ASCII: 3A 30 31 30 46 30 30 34 38 41 35 0D 0A (ASCII)

g. 10 Write multi-data register

Send the data format:

“:” ADDRESS 0x10 ADDRH ADDRL NUMH NUML BYTECOUNT DATAH1

DATAL1 DATA2H DATA2L – DATANH DATANL LRC 0X0D 0X0A

NUM: 0X0000 – 0X0000 – 0XFFFF; NUM: 0X000-0X00FF (NUM means the

number of data register)

BYCOUNT = NUM * 2

The format of correct returned data:

“:” ADDRESS 0x10 ADDRH ADDRL NUMH NUML LRC 0X0D 0X0A

The format of wrong returned data:

“:” ADDRESS 0X90 01 or 02 or 03 or 04 LRC 0X0D 0X0A

If 1.84 is input into Pd003 and 0.2 into Pd004 simultaneously

Data sent through RTU: 01 10 00 00 00 02 04 0B B8 00 02 D6 0D 0A (hexadecimal)

Data sent through ASCII: 3A 30 31 31 31 30 30 30 33 30 30 32 30 34 30 30 42 38 30

30 30 32 32 43 0D 0A (ASCII)

Data returned through RTU: 01 10 00 03 00 02 B1 C8 0D 0A (hexadecimal)

Data returned through ASCII: 3A 30 31 31 30 30 30 33 30 30 30 32 45 41 0D 0A

(ASCII)

The data sent to be input into 16-byte data “0x00b8” AND “0x02” means 1.84 and 0.2

are input respectively.

Wrong communication codes:

01 Illegal function code

02 Illegal data address

03 Illegal data

04 Device failures

Introduction of function codes

| Introduction of function data codes Data | Description | R/W | Note |
| --- | --- | --- | --- |
| 0000 | Reserved | R |  |
| 0001 | Reserved | R |  |
| 0002 | Reserved | R |  |
| 0003 | Running | R | 0-Stop 1-Run |
| 0004 | Jogging | R | 0 -Invalid 1 –Jogging |
| 0005 | FOR./REV. Rotation | R | 0-FOR 1-REV |
| 0006 | Braking | R | 0 –Invalid 1 -Brake P02-00=0 |
| 0007 | Frequency track | R | 0–Invalid 1-Frequency track P02-00=0 |
| 0008 | IGBT Short circuit | R | 0 -Invalid1 -Error ‘OC’ |
| 0009 | CT over-current detect high | R | 0 -Invalid1 -Error ‘OC’ |
| 000A | CT over-current detect low | R | 0 -Invalid1 -Error ‘OC’ |
| 000B | Earth short circuit | R | 0 -Invalid1 -Error ‘GF’ |
| 000C | Over-voltage | R | 0 -Invalid1 -Error ‘OU’ |
| 000D | Fuse break | R | 0 -Invalid1 -Error ‘FB’ |
| 000E | Low-voltage | R | 0 -Invalid1 -Error ‘LU’ |
| 000F | Inverter over-heating | R | 0 -Invalid1 -Error ‘OH’' |
| 0010 | Inverter over-load | R | 0 -Invalid1 -Error ‘OL’ |
| 0011 | Motor over-load | R | 0 -Invalid1 -Error ‘OA’' |
| 0012 | Motor over-torque | R | 0 -Invalid1 -Error ‘OT’ |
| 0013 | Connector fault | R | 0 -Invalid1 -Error ‘LU’ |
| 0014 | Braking pipe fault | R | 0 -Invalid1 -Error ‘BT’ |
| 0015 | CPU fault | R | 0 -Invalid1 -Error ‘FE’ |

Introduction of data register code functions

The function code addresses are same as the parameters shown on the keyboard.

Introduction of input register code function addresses

| 4) DATA: data content: n x 8-bit 0016 | Register fault | R | 0 -Invalid1 -Error ‘BE’ |
| --- | --- | --- | --- |
| 0017 | Master fault indication | R | 0 -Invalid1 -Error ‘KE’ |
| 0018 | Inverter over-load | R | 0 -Invalid 1 -Alarm OL’ |
| 0019 | Motor over-load | R | 0 -Invalid 1 -Alarm 'OA' |
| 001A | Motor over-torque | R | 0 -Invalid 1 -Alarm 'OT' |
| 001B | Temperature too high | R | 0 -Invalid 1 -Alarm 'OH' |
| 001C | Emergency stop | R | 0 -Invalid 1 -Alarm 'ES' |
| 001D | CRC inspection | R | 0 -Invalid 1 -Alarm 'ER’ |
| 001E | 4- 20MA break | R | 0 -Invalid 1 -Alarm ‘20’ |
| 001F | Para setting wrong | R | 0 -Invalid 1 -Alarm ‘PR’ |
| 0020 | Multi-input FB | R | 0—Invalid 1 一 Valid |
| 0021 | Multi-input MCS | R | 0—Invalid 1 一 Valid |
| 0022 | 01Terminal input | R | 0—Invalid 1 一 Valid |
| 0023 | 02Terminal input | R | 0—Invalid 1 一 Valid |
| 0024 | 03Terminal input | R | 0—Invalid 1 一 Valid |
| 0025 | 04Terminal input | R | 0—Invalid 1 一 Valid |
| 0026 | 05Terminal input | R | 0—Invalid 1 一 Valid |
| 0027 | 06Terminal input | R | 0—Invalid 1 一 Valid |
| 0048 | RUN | W | 0000—Invalid FF00—Valid |
| 0049 | FOR | W | 0000—Invalid FF00—Valid |
| 004A | REV | W | 0000—Invalid FF00—Valid |
| 004B | STOP | W | 0000—Invalid FF00—Valid |
| 004C | F/R | W | 0000—Invalid FF00—Valid |
| 004D | JOG | W | 0000—Invalid FF00—Valid |
| 004E | JOGF | W | 0000—Invalid FF00—Valid |
| 004F | JOGR | W | 0000—Invalid FF00—Valid |

| Input register address | Description | R/W | Note |
| --- | --- | --- | --- |
| 0000 | Output frequency | R |  |
| 0001 | Set frequency | R |  |
| 0002 | Output current | R |  |
| 0003 | Output rotation | R |  |
| 0004 | DC voltage | R |  |
| 0005 | AC voltage | R |  |
| 0006 | Counter | R |  |
| 0007 | Temperature | R |  |
| 0008 | PID target value | R |  |
| 0009 | PID feedback value | R |  |

5) LRC:

ASCII mode: Get LRC methods is that add ADDR to the last data, if the result is more

than 256,then the result subtract 256 until the result is less then 256 (if the result is

11128H, take 1128H) ,then 100H subtract the result to get LRC.

2. RTU mode

CRC calculating method of the check codes is the same as that of CRC.

Eg. Write 30.00Hz to inverter of 03

Sent data: 01H 06H 00H 03H 0BH B8H 8EH 88H

Pd170

Display Items

Set Range: 0-5                   Unit: 1  Factory Setting: 0

This parameter is only valid when Bit 2 is set to 1 in CD168.

For the details, refer to Pd171.

0: Inverter Temperature

1: Counter Value

2 PID Target Value

3: PID Feedback Value

Pd171

Display Items Open

Set Range: 0-15                   Unit: 1 Factory Setting: 0

This parameter is set for selection of displaying of DC voltage, AC voltage and other

items, so that the customer can monitor and view them in sequence through the switch

key.

It can be set first in the binary 3 bits mode, and then converted to a decimal value.

In the contents displayed the factory setting is to show output frequency, set frequency,

output current and output revolution through the switch key. If it is necessary to view

| ADDR | FUNCL | DATAH(ADDRESS) | DATAL(ADDRESS) | DATAH | DATAL | CRCH | CRCL |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01H | 06H | 00H | 03H | 0BH | B8H | 8EH | 88H |

| Quiet | ADDR | FUNCL | DATAH | DATAL | CRCH | CRCL | Quiet |
| --- | --- | --- | --- | --- | --- | --- | --- |
| > 50ms |  |  |  |  |  |  | > 50ms |

and monitor other items, they can be set through Pd170 and Pd171.

Pd172

Fault Clear

Set Range: 00-10

01 is for fault clear. Others have no function.

Unit: 1 Factory Setting: **

Pd173

Inverter Voltage Class

Unit: 1V Factory Setting: *

It is factory setting, and is decided by the model. It can be observed, but not set.

Pd174

Inverter Current Class

Unit: 1A Factory Setting: *

It is decided by the model and can not be changed.

Pd175

Inverter Model

Set Range: 0-1                   Unit: 1  Factory Setting: 0

0: Constant torque   1: For kinds of fan. It can be observed, but not changed.

Pd176

Inverter Frequency Standard

Unit: 1

Factory Setting: *

0: 50Hz

1: 60Hz   It is factory setting. It can be observed, but not set.

Pd177

Pd178

Fault Record 1

Fault Record 2

Factory Setting: ————

Factory Setting: ————

Pd179         Fault Record 3               Factory Setting: ————

Pd180         Fault Record 4               Factory Setting: ————

When it has no fault record it shows ----. After access to this parameter, the fault

display can be checked.

Pd181

Software Version

Factory Setting: *

It can be observed, but not set.

Pd182

Manufacture Date

Factory Setting: *

It is factory setting. It can be observed, but not set.

Pd183

Serial No.

Factory Setting: *

It is factory setting. It can be observed, but not set.

Pd183~Pd250 Factory Setting

Note: * means the said parameter has a variety of set values or should be set

specifically according to concrete conditions

** means the said parameter can be set during the operation.

X. Care & Maintenance, Fault Information and Troubleshooting

Periodical maintenances and inspections will keep your inverter in its normal state for

long time.

1. Precautions about Inspection and Maintenance











2.



















3.

Be sure to turn off the power supply to the inverter (R.S.T) first before the

inspection and maintenance.

After confirming the main circuit power supply has been turned off and the

display has disappeared, wait until the internal indicator lamp for high voltage

goes out before performing the inspection and maintenance.

During the inspection, do not pull out or wrongly distribute the internal power

supply, wires and cables. Otherwise it will cause malfunction or damage to the

inverter.

Do not leave any screw or other part inside the inverter during the installation, or

it will result in the short circuit of circuit board.

Keep the inverter clean, free from dust, oil mist and moisture after the

installation.

Periodical Inspection and Maintenance items

Check whether the power supply voltage conforms to the rated voltage of the

inverter.

(Pay special attention to that whether there is any damage on the power supply

wires and the motor.)

Check whether the wiring terminals and the connectors are tight.

(Check whether the power supply wires and terminal connection wires have any

broken strand).

Check whether there is dust, iron filings or corrosive fluid in the inverter.

Measuring the insulation impedance of the inverter is forbidden.

Examine the output voltage, output current and output frequency of the inverter.

(The measuring results should not have too big difference.)

Check whether the ambient temperature of the inverter is between -5°C and

40°C and whether the installation environment has good ventilation.

Check whether the humidity is kept below 90% (without condensation).

Check whether the motor makes unusual noises or abnormal vibration in running.

(The inverter should not be installed in a place with high vibration.)

Please make periodical cleaning of vent holes.

Fault Indication and Troubleshooting

The inverter of RLP series is relatively perfective with the protection functions of

overload, inter-phase short circuit, earth short circuit, under-voltage, overheating and

over-current, etc. When a protection function happens with the inverter, please check

the reasons of faults according to the information listed in the table below. The

inverter can be restarted after the disposal. If the fault cannot be disposed, please

| contact the local distributor. Fault Display | Fault Contents & Description | Disposal methods |
| --- | --- | --- |
| E.OC.A | Over-current during ramp-up | 1: Check whether the motor has got short circuit or partial short circuit and whether the insulation of output wire is good. 2: Extend the ramp-up time. 3: The configuration of the inverter is not reasonable. The inverter's capacity should be increased. 4: Decrease the torque and increase the set value. |
| E.OC.n | Over-current at constant speed | 1: Check whether the motor has got short circuit and whether the insulation of the output wires is good. 2: Check whether the motor is blocked and whether there is a sudden change of mechanical load. 3: Check whether the inverter's capacity is too small and increase its capacity. 4: Check whether there is a sudden change in the power supply voltage. |
| E.OC.d E.OC.S | Over-current at decel Over-current at stop | 1: Check whether the insulation of the output wires is good and whether the motor has got short circuit. 2: Extend the Ramp-down Time. 3: Replace it with an inverter of larger capacity. 4: DC braking is too high. Decrease DC braking. 5: The inverter has failure. Please send it to the factory for repair. |
| GF | Short circuit | 1: Check whether the connection wire of the motor has got short circuit. 2: Check whether the insulation of the output wires is good. 3: Please send it for repair. |
| E.OU.S E.OU.a E.OU.n E.OU.d | Over-voltage at stop Over-voltage at accel Over-voltage at constant speed Over-voltage at decel | 1: Extend the Ramp-down Time or add a braking resistor. 2: Improve the mains supply voltage and check whether there is any sudden change in the voltage. |
| Fb | Fuse break | The fuse breaks. Please send it for repair. |

Code Comparison Table:

4. Faults and Analysis

(1) When RUN key is pressed, the motor does not run.

1) The setting of operation mode is wrong, i.e., under the operation mode of

external control terminals, the inverter is started by the digital operator or

under the operation mode of the digital operator; it is started by the external

control terminals.

| OH | Overheat of Inverter | 1: Check whether the fan is blocked and whether there is any foreign matter stuck in the cooling fins. 2: Check whether the ambient temperature is normal. 3: Check whether there is enough space for ventilation and good air convection. |
| --- | --- | --- |
| OL | Inverter overload, 150% per 1min | 1: Check whether the capacity of the inverter is lower. Otherwise it should be increased. 2: Check whether there is any jamming in the mechanical load. 3: The setting of V/F curve is bad. Set it again. |
| OA | Motor overload, 150% per 1min | 1: Check whether there is any sudden change in the mechanical load. 2: The equipped motor is too small. 3: The motor is hot and the insulation becomes bad. 4: Check whether the voltage has big fluctuation. 5: Check whether there is any phase missing. 6: The mechanical load is increased. |
| OT Motor over-torque 1: Check whether there is any fluctuation in the mechanical load. 2: Check whether the equipped motor is smaller. |  |  |

| Er | External interference | Isolate the interference source |
| --- | --- | --- |
| ES | Emergency Stop | In Emergency Stop |
| 20 | 4-20mA wire broken | Join the broken wire |
| Pr | Setting error | Correct the setting |
| DCb | DC brake status | In DC braking |

2) The frequency reference is too low or not set.

3) The peripheral wiring is wrong. For example, the setting of wiring of two- wire

system and three-wire system and other related parameters have errors.

4) The setting of multi-function terminals is wrong (in the external control).

5) The inverter is in the fault protection.

6) The motor fails.

7) The inverter fails.

(2) The parameters cannot be set.

1) Password locks. Please decrypt it first before resetting.

2) The inverter is in running.

3) The connection of the connecting parts is abnormal. The communication of the

digital operator is abnormal. Take out the operator after power-off and then

mount it again for a trial.

(3) The motor cannot rotate reverse.

Reverse rotation is disabled.

(4) The motor rotates in the opposite direction.

The output line is wrongly connected. Please change any two lines of U.V.W over.

(5) The deceleration of the motor is too slow.

1) The setting of Ramp-down Time is too long. Decrease Ramp-down Time.

2) Add a braking resistor.

3) Add a DC brake.

(6) Over-heat of the motor

1) The load is too large. The actual torque has exceeded the rated torque of the

motor. It is recommended to increase the capacity of the motor.

2) The ambient temperature is too high. In a place with higher temperature the

motor will be burn out. Please decrease the temperature around the motor.

3) The phase to phase withstand voltage of the motor is insufficient. The switch

actions of the inverter will make the winding coil of the motor produce shock

wave. Typically the maximum shock voltage will reach 3 times that of input

power of the inverter. Please select a motor with higher phase to phase

withstand voltage against shock than the maximum shock voltage.

(7) The starting of the inverter interferes with other control devices

1) Decrease the carrier frequency and reduce the number of actions of internal

switches.

2) Install a noise filter at the power input of the inverter.

3) Install a noise filter at the output of the inverter.

4) Make correct grounding for the inverter and the motor.

5) Use metal conduit to tube the cable to shield it.

6) Make separate wiring for the main circuit wires and control wires.

(8) When the fan starts the inverter detected an over-current stall.

1) At start the fan rotates idly. Please set it for DC braking at start.

2) When DC braking at start has been set, increase the DC braking value.

(9) The machine has the noise of vibration or roar

1) The vibration frequency of mechanical system resonates with the carrier. Adjust

the carrier to avoid the point of resonance.

2) The vibration frequency of mechanical system resonates with the output

frequency of the inverter.

a. Set it for skip function to avoid the point of resonance.

b. Put rubber vibration isolator on the base plate of motor.

Common abnormities and solutions

| The analysis and measures for the common abnormities refer to the following table: Abnormity |  |  | Possible Causes and Solutions |
| --- | --- | --- | --- |
| Mot or Not Run | No display on keyboard | Examine whether the power supply is on, the input power has phase or is connected correctly |  |
| Mot or Not Run | The keyboard does not display, but the charge indicator lamp is ON | Examine the wires of the keyboard and the socket; Measure the voltage of controlled power supply, so as to confirm whether the switch power is running normally; If the switch power is not running properly, examine whether the socket of switch power inlet (P, N) is connected well, whether the vibration resistance is damaged or the stabilizing pipe is normal. |  |
| Mot or Not Run | No voltage of low voltage of PN terminal | Examine the charging return circuit. |  |
| Mot or Not Run | Motor buzz | The motor is under heavy load, please try to reduce the load. |  |
| Mot or Not Run | No abnormity is found | Check whether the inverter is in the state of trip or has not been reset after trip; whether it is in the state of restart after power break; whether the keyboard is reset; whether it accesses to the program running state or the multi-speed running state. For the running state or non-running state, use the method of restoring the factory setting to confirm whether the running command is given. Examine whether the running frequency is set as 0. |  |
| Motor can not accelerate or decelerate smoothly |  |  | Inappropriate setting of ramp time; Too low current amplitude; Over-voltage protection during deceleration; Inappropriate setting of carrier frequency, over-load or vibration appears |

| Too high or too low motor rotation speed | Inappropriate V/F feature selection; Incorrect V/F feature level selection, to be reset; Substandard or non-standard rated voltage of motor; Too low voltage of power supply; Incorrect setting of frequency set signal gain; Incorrect setting of output frequency. |
| --- | --- |

XI. Selection of Peripheral Devices and Disposition

1. Options

Description

Functions

NFB or Ground fault interrupter for Protect the wiring of the inverter. Be sure to

wire connection

install a breaker at the power. Please select a

ground fault

circuit  interrupter against

high-order harmonics.

Electromagnetic contactor

Surge absorber

Isolating transformer

In order to prevent the braking resistor from

burning out, please add an electromagnetic

contactor and connect a surge absorber to the

coil when using it.

Absorb the switching surge current from the

electromagnetic contactor and control relays.

Its function of isolating the input and output of

the

inverter is effective to reduce the

interference to other electric devices.

DC reactor

AC reactor

Braking resistor, braking unit

Improve the input power factor of the inverter.

Improve the input power factor of the inverter

and prevent the shock of surge voltage.

Consume the regenerating energy of the motor

and shorten the ramp-down time.

1) Leakage switch

There is earth static capacity inside of the inverter and the motor as well as the input

and output leads. Due to higher carrier frequency of the inverter, the inverter has

higher earth leakage current, especially for the inverters of large capacity series.

When using a leakage switch, it may sometimes result in the error action of the

protective circuit. So when using a leakage switch, attention should be paid to its

selection and the proper reduction of carrier frequency and shortening the leads, etc.

2) AC reactors

An AC reactor can constrict the high-order harmonic of input current of the inverter to

improve its input power factor and prevent the shock of surge. It is recommended to

use an input AC reactor under the following circumstances:

a: Three-phase power supply is in unbalance.

b: Any equipment with thyristor or power factor compensation unit with switching

control is connected to the same power supply.

3) DC reactors

It is necessary to install a DC reactor when the capacity of power supply is more than

1000 KVA or the mains power capacity is higher than the rated capacity of the

inverter. A DC reactor is also needed for the case with higher demand on the

improvement of power factor of power supply. This DC reactor can be used together

with an AC reactor to achieve the obvious effect of decreasing high-order harmonic at

input. If it is necessary to install a DC reactor, please contact the local distributor.

2. Disposition

1) DC Reactors Disposition

Connection: (1) Remove the jumpers of P and P1 terminals.

(2) Connect DC reactor to Terminals P and P1 as shown in the following

diagram:

Note: RLP inverter of above 37KW has connectors. The inverter of below 37KW must

not be connected with it.

The function of DC reactor is to restrict the AC component stacked with DC reactor to

a specified value to suppress the mains harmonics and improve the power factor of the

inverter.

2) AC Reactors Disposition

| Inverter Model | Matched Power (W) | Rated Current(A) | Inductance (mH) |
| --- | --- | --- | --- |
| DCL-37 | 37 | 100 | 0.7 |
| DCL-45 | 45 | 120 | 0.58 |
| DCL-55 | 55 | 146 | 0.47 |
| DCL-75 | 75 | 200 | 0.35 |
| DCL-90 | 90 | 238 | 0.29 |
| DCL-110 | 110 | 291 | 0.24 |
| DCL-132 | 132 | 326 | 0.215 |
| DCL-160 | 160 | 395 | 0177 |
| DCL-200 | 200 | 494 | 0142 |
| DCL-220 | 220 | 557 | 0126 |
| DCL-280 | 280 | 700 | 010 |
| DCL-300 | 300 | 800 | 0.08 |
| DCL-315 | 315 | 800 | 0.08 |
| DCL-345 | 345 | 660 | 0.07 |
| DCL-375 | 375 | 715 | 0.064 |
| DCL-400 | 400 | 765 | 0.058 |
| DCL-415 | 415 | 795 | 0.053 |

| Inverter Model Matched Power Rated Current(A) Inductance (mH) (W) HKSG2-24 11 24 0.52 HKSG2-34 15 34 0.397 HKSG2-38 18.5 38 0.352 |  |  |  |
| --- | --- | --- | --- |
| HKSG2-50 | 22 | 50 | 0.26 |
| HKSG2-60 | 30 | 60 | 0.24 |

The incoming reactor is also named shift-changing reactor and it is used for the

incoming wire of the mains with AC flowing inside. Its function is to suppress the

harmonics of the inverter feedback to the mains.

| HKSG2-75 | 37 | 75 | 0.235 |
| --- | --- | --- | --- |
| HKSG2-91 | 45 | 91 | 017 |
| HKSG2-112 | 55 | 112 | 016 |
| HKSG2-150 | 75 | 150 | 0112 |
| HKSG2-180 | 90 | 180 | 010 |
| HKSG2-220 | 110 | 220 | 0.09 |
| HKSG2-265 | 132 | 265 | 0.08 |
| HKSG2-300 | 160 | 300 | 0.07 |
| HKSG2-360 | 200 (185) | 360 | 0.06 |
| HKSG2-400 | 220 | 400 | 0.05 |
| HKSG2-560 | 280 | 560 | 0.03 |
| HKSG2-640 | 315 | 640 | 0.0215 |
| HKSG2-700 | 345 | 700 | 0.019 |
| HKSG2-750 | 375 | 750 | 0.017 |
| HKSG2-800 | 400 | 800 | 0.015 |
| HKSG2-860 | 415 | 860 | 0.012 |

| Inverter Model | Braking resistor specification |  | Braking torque 10%ED | Special Motor KW |
| --- | --- | --- | --- | --- |
| Inverter Model | W |  | Braking torque 10%ED | Special Motor KW |
| RLPA00D423B | 80 | 200 | 125 | 0.4 |
| RLPA0D7523B | 100 | 200 | 125 | 0.75 |
| RLPA01D523B | 300 | 100 | 125 | 1.5 |
| RLPA02D223B | 300 | 70 | 125 | 2.2 |
| RLPA0D7543B | 80 | 750 | 125 | 0.75 |
| RLPA01D543B | 300 | 400 | 125 | 1.5 |
| RLPA02D243B | 300 | 250 | 125 | 2.2 |
| RLPA03D743B | 400 | 150 | 125 | 3.7 |
| RLPA05D543B | 500 | 100 | 125 | 5.5 |
| RLPA07D543B | 1000 | 75 | 125 | 75 |
| RLPA001143B | 1000 | 50 | 125 | 11 |

For the braking resistor used for the machines of above 315 KW,

please contact the factory.

For the inverter of above 11KW to realize quick brake, a braking unit must be added.

Note: 1: Please select the resistor value and operating frequency given by our

company.

2: If it causes any damage to the inverter and other devices due to the use of any

braking resistor and braking model group not supplied by our company, we

will take no responsibility.

3: Be sure to consider the safety and ignitability of the environment when

installing a braking resistor. The distance to the inverter should be at least

100 mm.

4: If it is necessary to change the resistor value and power value, please contact

the local distributor.

5: In need of a braking resistor a separate order must be placed. Please contact

| the local distributor for details. RLPA001543B | 1500 | 40 | 125 | 15 |
| --- | --- | --- | --- | --- |
| RLPA18D543B | 4800 | 32 | 125 | 18.5 |
| RLPA002243B | 4800 | 272 | 125 | 22 |
| RLPA003043B | 6000 | 20 | 125 | 30 |
| RLPA003743B | 9600 | 16 | 125 | 37 |
| RLPA004543B | 9600 | 13.6 | 125 | 45 |
| RLPA005543B | 12000 | 20/2 | 125 | 55 |
| RLPA007543B | 18000 | 13.6/2 | 125 | 75 |
| RLPA009043B | 18000 | 20/3 | 125 | 90 |
| RLPA011043B | 18000 | 20/3 | 125 | 110 |
| RLPA013243B | 24000 | 20/4 | 125 | 132 |
| RLPA016043B | 36000 | 13.6/4 | 125 | 160 |
| RLPA018543B | 45000 | 13.6/5 | 125 | 185 |
| RLPA020043B | 45000 | 13.6/5 | 125 | 200 |
| RLPA022043B | 48000 | 13.6/5 | 125 | 220 |
| RLPA025043B | 48000 | 13.6/5 | 125 | 250 |
| RLPA028043B | 57600 | 13.6/6 | 125 | 280 |
| RLPA030043B | 57600 | 13.6/6 | 125 | 300 |

XII. Appendices

Appendix 1: Simple Examples of Application

1. Disturbance Function (Generation of Triangle Wave)

2. Drawing Function

Parameter setting:

Pd081=4      Pd003=25    Pd086=50    Pd087=30

Pd101=720    Pd046=29    Pd001=1

Note: (1) When triggered by external multi-function terminals (as RST in the

diagram), the drawing action starts to be implemented.

(2) In implementation of drawing action the running time T=P101*10S

3. FOR/REV Rotation of the Motor Controlled by One Potentiometer

4. Internal Control 8 Speed Run

A curve as shown in the following diagram is established. Internal control 8-speed run

will stop after running for one cycle.

Note: 1.The running time of each speed is set by Pd101-Pd108=15;

2. Auto cycling Pd081=1;

3. After the running command is given, it will run with the set curve for one

cycle and stop.

5. Simple Water Supply with Constant Pressure

① Use a pressure transmitter with measuring range of 0-10kg, feedback of 4-20mA,

requiring water supply at the pressure of 5kg with alarming at the upper limit of 6kg

and the lower limit of 4kg. The start from the panel stops.

Note: Pd156, Pd157 and Pd158 should be set according to the actual conditions. For

general water supply with constant pressure, Pd150=80~100, Pd151=2.5~3, Pd152=0.

② For a resistance transmission pressure gauge of 0~10kg, it is required to control

operation and stop by external terminals and give a target value through a

potentiometer.

Attention:

(1) The target value of RLP series inverter can be selected in two ways, one is

to set it on the panel and another is the analog of 0~10V;

(2) The feedback signal is 4-20mA. Others are invalid;

(3) In this example the target value is given by the potentiometer (0~10V) ;

(4) Pd156, Pd157 and Pd158 should be set according the actual condition.

(Refer to the parameter description.)

(5) The special panel for PID is designed according to general resistance

transmission pressure gauge with input internal resistance converting to

the standard signal in 0-400Q. When the resistance value of the resistance

transmission pressure gauge used by the customer exceeds the specified

range, please change the resistance transmission pressure gauge or

connect a resistor in parallel for correction.

(6) Output resistance values vary with different manufacturers of resistance

transmission pressure gauge. After conversion, the levels of current signal

are different. The user can set a target value consistent with its actual

conditions by themselves.

(7) The target value is given by the potentiometer. Pd002 must be set as 1,

otherwise PID will not work.

6. Example common application of analog and multi-speed:

Requirement: Speed 1 is given frequency by analog. Use a switch to switch it and turn

to external control multi-speed run.

Action Description: (1)

(2) The switching of forward and reverse rotation can be implemented through either

multi-function terminals or the FOR/REV key on the panel. (In this example, the

switching is made through the panel)

7. Example application of Auto PLC Suspend

Requirement: Auto PLC can be suspended during the internal control multi-speed run.

| K1 State | K2 State | Operating Frequency |
| --- | --- | --- |
| OFF | OFF | Given by a potentiometer |
| ON | OFF | Speed 2 ( 15Hz ) |
| OFF | ON | Speed 3 ( 30Hz ) |
| ON | ON | Speed 4 ( 25Hz ) |

After handling the related problems, it can resume.

(1) Connection

(2). Parameters: Pd001=1 D1 terminal control operation

Pd049=31 SPL terminal is set for Auto PLC reset suspend function.

Pd117=1 Auto PLC Memory

Pd081=1 Cycling run

Pd080=1 Internal control multi-speed

Pd086=15   Pd088=20   Pd086=25    Pd003=10

Pd101=10   Pd102=10   Pd103=10    Pd104=10

(3) Operating curve:

(4) Operation description

① (K1) D1 is closed and the inverter will run according to the program set by

internal control multi-speeds.

②When it is required to stop due to fault and process or other reasons, K1 will be

opened. And the inverter will stop output and suspend counting time. After the

fault is removed, K1 will be closed and the inverter will continue to run according

to original program.

③ When it is required to run again from the beginning due to fault and process stop,

K1 should be opened. Press K2 to reset. By closing K1, it will restart to run.

8. Application example of plastic injection machine

Control principle diagram

Note: Places marked with ‘*” are to be decided upon the concrete conditions.

When the inverter is under operation, please do not shift the switch. When it has

to be shifted, make sure the inverter stops the output.